## Request a quote
Request a quotation for LKSM-HF & LKSM-SHF2 0.6/1 KV
Share governing standard (IEC/NEK/BS/IEEE/JIS/VG), voltage rating, core count × cross-section, armour/sheath type (SHF1/SHF2/SW4/Type P) and total length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/lksm-hf-lksm-shf2-0-6-1-kv/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
LKSM-HF & LKSM-SHF2 0.6/1 kV IEC 60092-353 Copper-Braided Marine & Off – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lksm-hf-lksm-shf2-0-6-1-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| LKSM-HF 3×16+1G16 mm² | 3 × 16 + 1G16 mm² (4G16) | IEC 60228 Class 2/5 Cu/SnCu | 22.4 | 920 | 3.8 | 135 | LKSM-HF & LKSM-SHF2 0.6/1 KV Construction Schedule (−40…+90 °C)
| LKSM-HF 3×35+1G16 mm² | 3 × 35 + 1G16 mm² (4G35) | IEC 60228 Class 2/5 Cu/SnCu | 28.8 | 1690 | 7.4 | 175 | LKSM-HF & LKSM-SHF2 0.6/1 KV Construction Schedule (−40…+90 °C)
| LKSM-HF 3×70+1G35 mm² | 3 × 70 + 1G35 mm² (4G70) | IEC 60228 Class 2/5 Cu/SnCu | 38.2 | 3260 | 14.8 | 230 | LKSM-HF & LKSM-SHF2 0.6/1 KV Construction Schedule (−40…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A.

## Electrical, optical & thermal p
LKSM-HF & LKSM-SHF2 0.6/1 kV IEC 60092-353 Copper-Braided Marine & Off – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lksm-hf-lksm-shf2-0-6-1-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 16 + 1G16 mm² (4G16) | 1.15 | 0.6/1 kV (98 A) | −40…+90 °C
3 × 35 + 1G16 mm² (4G35) | 0.524 | 0.6/1 kV (158 A) | −40…+90 °C
3 × 70 + 1G35 mm² (4G70) | 0.268 | 0.6/1 kV (245 A) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
LKSM-HF & LKSM-SHF2 0.6/1 kV IEC 60092-353 Copper-Braided Marine & Off – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/lksm-hf-lksm-shf2-0-6-1-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per IEC 60092-353)
Key data | Operating temp. | −40…+90 °C (Continuous shipboard & offshore service)
Key data | Min. bend radius | 6 × OD (Marine tray, bulkhead & deck routing)
Key data | Core / conductor | Stranded Copper (IEC 60228 Class 2 / Class 5 annealed cop)
Key data | Outer protection | SHF1 / Cross-Lin (Black halogen-free polyolefin (SHF1) or )
Key data | Standard | IEC 60092-353 (IEC 60092-353 / IEC 60092-360 SHF1 & SHF)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A)
Electrical | Core / conductor construction | Stranded Copper Conductors (7G2.5 mm²) — IEC 60228 Class 2 / Class 5 annealed copper conductors
Electrical | Primary dielectric / buffering | Number-Coded XLPE Insulation — White XLPE cores printed 1–6 plus Green/Yellow earth conductor
Thermal | Continuous operating temperature | −40…+90 °C (shipboard & offshore duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | SHF1 / Cross-Linked SHF2 Outer Sheath — Black halogen-free polyolefin (SHF1) or oil-resistant elastomer (SHF2)
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Armour, screen & mechanical duty | Tinned Copper Braid Armour (LKSM) — High-density tinned copper wire braid for mechanical & EMC protection
Resistance | Flame, fire & smoke performance | Qualified for marine flame-retardance and low-smoke zero-halogen / fire safety per IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A
Resistance | Oil, drilling mud & seawater resistance | Resistant to marine fuel/lube oils, salt mist and offshore fluids per IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A
Standards | Environmental & test standards | IEC 60228 / IEC 60332-3-22 / IEC 60754 / IEC 61034 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | LKSM-HF & LKSM-SHF2 0.6/1 KV
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (SHF1 / Cross-Lin)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
LKSM-HF & LKSM-SHF2 0.6/1 kV IEC 60092-353 Copper-Braided Marine & Off – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/lksm-hf-lksm-shf2-0-6-1-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded Copper Conductors (7G2.5 mm²) | IEC 60228 Class 2 / Class 5 annealed copper conductors
2 | Number-Coded XLPE Insulation | White XLPE cores printed 1–6 plus Green/Yellow earth conductor
3 | Halogen-Free Bedding Layer | Extruded flame-retardant halogen-free filler and tape bedding
4 | Tinned Copper Braid Armour (LKSM) | High-density tinned copper wire braid for mechanical & EMC protection
5 | SHF1 / Cross-Linked SHF2 Outer Sheath | Black halogen-free polyolefin (SHF1) or oil-resistant elastomer (SHF2)
| LKSM-HF & LKSM-SHF2 0.6/1 KV — Standard Shipboard & Offshore Execution | Built to IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A with stranded copper conductors (7g2.5 mm²) and shf1 / cross-linked shf2 outer sheath
| LKSM-HF & LKSM-SHF2 0.6/1 KV — Custom Drum Length & Gland Kit | Available in custom continuous shipboard/offshore drum lengths or with marine EMC cable glands
| LKSM-HF & LKSM-SHF2 0.6/1 KV — Class & Routine Test Certified | Supplied with EN 10204 3.1 routine dielectric, conductor resistance & flame/fire test report

## Quality and supply
LKSM-HF & LKSM-SHF2 0.6/1 kV IEC 60092-353 Copper-Braided Marine & Off – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/lksm-hf-lksm-shf2-0-6-1-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A) — DC resistance at 20 °C / optical attenuation and outer diameter within IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Flame, fire integrity, oil/mud & mechanical qualification (IEC 60092-353 / IEC 60092-360 SHF1 & SHF2 / IEC 60332-3-22 Cat. A) — Verified flame/fire performance, fluid resistance and thermal stability across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60092-353 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX LKSM-HF & LKSM-SHF2 0.6/1 KV IEC 60092-353 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel marine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shipboard/offshore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP