## Request a quote
Request a quotation for LSX Unarmoured
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for LSX Unarmoured.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/lsx-unarmoured-lszh-single-conductor-shipboard-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
LSX Unarmoured LSZH Single-Conductor Shipboard Power Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lsx-unarmoured-lszh-single-conductor-shipboard-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| LSX Unarmoured 1C × 16 mm² (6 AWG) 0.6/1 kV | 1 × 16 mm² (6 AWG) | 16.0 mm² | 8.4 | 148 | 195 | 50 | Standard LSX Unarmoured configurations
| LSX Unarmoured 1C × 35 mm² (2 AWG) 0.6/1 kV | 1 × 35 mm² (2 AWG) | 35.0 mm² | 11.4 | 325 | 405 | 68 | Standard LSX Unarmoured configurations
| LSX Unarmoured 1C × 70 mm² (2/0 AWG) 0.6/1 kV | 1 × 70 mm² (2/0 AWG) | 70.0 mm² | 15.2 | 650 | 775 | 91 | Standard LSX Unarmoured configurations
| LSX Unarmoured 1C × 120 mm² (4/0 AWG) 0.6/1 kV | 1 × 120 mm² (4/0 AWG) | 120.0 mm² | 19.3 | 1110 | 1290 | 116 | Standard LSX Unarmoured configurations
| LSX Unarmoured 1C × 185 mm² (373 kcmil) 2.0 kV | 1 × 185 mm² (373 kcmil 2kV) | 185.0 mm² | 24.1 | 1720 | 1980 | 145 | Standard LSX Unarmoured configurations
| LSX Unarmoured 1C × 300 mm² (646 kcmil) 2.0 kV | 1 × 300 mm² (646 kcmil 2kV) | 300.0 mm² | 30.2 | 2790 | 3160 | 181 | Standard LSX Unarmoured configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard).

## Electrical & ampacity
LSX Unarmoured LSZH Single-Conductor Shipboard Power Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lsx-unarmoured-lszh-single-conductor-shipboard-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
1 × 16 mm² (6 AWG) | 1.24 | 125 | 110 | 2.29 | 2.3 | 3500
1 × 35 mm² (2 AWG) | 0.565 | 205 | 182 | 5.01 | 1.08 | 3500
1 × 70 mm² (2/0 AWG) | 0.277 | 320 | 285 | 10.01 | 0.55 | 3500
1 × 120 mm² (4/0 AWG) | 0.164 | 455 | 405 | 17.16 | 0.35 | 3500
1 × 185 mm² (373 kcmil 2kV) | 0.108 | 595 | 530 | 26.46 | 0.25 | 6500
1 × 300 mm² (646 kcmil 2kV) | 0.0654 | 815 | 725 | 42.9 | 0.18 | 6500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard).

## Technical data
LSX Unarmoured LSZH Single-Conductor Shipboard Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/lsx-unarmoured-lszh-single-conductor-shipboard-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | IEEE 1580 Type (UL 1309 Marine Shipboard / IEEE 45)
Key data | Voltage rating | 0.6/1 kV & 2 kV (600 V, 1000 V & 2000 V classes)
Key data | Conductor | Flex Tinned Cu (Fine-stranded ASTM B33 / IEC Class 5)
Key data | Insulation/Jkt | 110 °C XLPO LSZH (Cross-linked low-smoke zero-halogen)
Key data | Cold bend/impact | -40 °C / -35 °C (CSA C22.2 No. 0.3 arctic marine)
Key data | Class approvals | ABS / DNV / USCG (Lloyd's Register & Transport Canada)
Electrical | Rated voltage | 600/1000 V (0.6/1 kV) & 2000 V (2.0 kV) per
Electrical | AC dielectric test voltage | 3.5 kV AC (0.6/1 kV) · 6.5 kV AC (2.0 kV)
Electrical | Insulation resistance constant Ki | ≥ 3.67 MΩ·km at 90 °C per IEEE 1580
Electrical | Max. conductor operating temp. | +100 °C / +110 °C (IEC/ABS/DNV) · +95 °C
Thermal | Ambient temperature range | -40 °C to +90 °C
Thermal | Cold bend & cold impact rating | -40 °C cold bend / -35 °C cold impact (CSA
Mechanical | Min. bending radius | 4 × D (D ≤ 25 mm) · 6 × D (D > 25 mm) per
Mechanical | Abrasion & crush resistance | High-modulus cross-linked Type LSX jacket
Resistance | Flame retardancy | IEEE 1202 / FT4 (70,000 BTU/hr) & IEC
Resistance | Halogen-free, low smoke & oil | IEC 60754-1/2 (< 0.5 % HCl) · IEC 61034-2 ·
Standards | Primary specification | IEEE 1580 Type LSX · IEEE 45 · UL 1309 ·
Standards | Marine approvals | ABS, DNV, Lloyd's Register, USCG, BV
Identification | Core / sheath colour | Black (Dark Grey, Red, Blue, or
Identification | Surface print legend | AWG/kcmil + metric mm², voltage, IEEE 1580

## Construction
LSX Unarmoured LSZH Single-Conductor Shipboard Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/lsx-unarmoured-lszh-single-conductor-shipboard-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible stranded tinned copper | Annealed tinned copper rope-lay flexible stranding per IEEE 1580 Table 3 / ASTM B33 | IEEE 1580 / UL 1309
2 | Separator tape | Halogen-free polyester tape for clean stripping at compression lugs | IEEE 1580
3 | Type LSX cross-linked polyolefin (XLPO) | Irradiation or silane cross-linked low-smoke zero-halogen polyolefin (100/110 °C dry, 90 | IEEE 1580 Type LSX
4 | Integral / outer LSX LSZH surface | Oil-, mud-, and sunlight-resistant low-smoke zero-halogen XLPO surface passing IEEE 1202 | UL 1309 / IEEE 1580
| Type LSX 600 V / 1000 V Single-Conductor | Unarmoured single-core shipboard power and switchboard cable from 14 AWG (2.5 mm²) to 777.7 kcmil (400 mm²).
| Type LSX 2000 V (2 kV) Heavy Propulsion Feeder | Increased insulation wall thickness for 690–1000 V AC VFD propulsion and 1,000–2,000 V DC drilling drives.

## Quality and supply
LSX Unarmoured LSZH Single-Conductor Shipboard Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/lsx-unarmoured-lszh-single-conductor-shipboard-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / IEEE 45 / UL 1309 (Type LSX Unarmoured Shipboard). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV / 6.5 kV AC dielectric & water-tank IR — IEEE 1580 Table 18 AC test for 5 min after 6 h water immersion | 100 % of reels
Routine test | DC conductor resistance @ 20 °C — IEEE 1580 Table 3 / IEC 60228 Class 5 tinned copper | 100 % of reels
Sample test | -40 °C cold bend & -35 °C cold impact — CSA C22.2 No. 0.3 / IEEE 1580 arctic flexibility | Per production batch
Type test | IEEE 1202 FT4 & IEC 60332-3-22 Cat A flame — Vertical tray flame, smoke index & < 0.5 % halogen acid gas | Class society approval
Standard / approval | IEEE 1580 Type LSX
Standard / approval | UL 1309 / IEEE 45
Standard / approval | ABS / DNV / LR / USCG
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX IEEE 1580 TYPE LSX UNARMOURED
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP