## Request a quote
Request a quotation for LiHCH
Application engineer · halogen-free EMC & signal cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/lihch-screened-lszh-signal-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
LiHCH Screened LSZH Signal Cable – Dimensions & weights (22)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lihch-screened-lszh-signal-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100 · LSZH EMC. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| LiHCH 2×0.14 | 2×0.14 | 26 | 3.7 | 4 | 12 | 22 | 24 | 0.14 mm² Screened LSZH Signal Configurations (350 V peak)
| LiHCH 4×0.14 | 4×0.14 | 26 | 4 | 4.4 | 16 | 31 | 26 | 0.14 mm² Screened LSZH Signal Configurations (350 V peak)
| LiHCH 8×0.14 | 8×0.14 | 26 | 5.2 | 5.7 | 26 | 51 | 34 | 0.14 mm² Screened LSZH Signal Configurations (350 V peak)
| LiHCH 12×0.14 | 12×0.14 | 26 | 5.9 | 6.4 | 34 | 69 | 38 | 0.14 mm² Screened LSZH Signal Configurations (350 V peak)
| LiHCH 2×0.25 | 2×0.25 | 24 | 4.2 | 4.6 | 16 | 30 | 28 | 0.25 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 4×0.25 | 4×0.25 | 24 | 4.7 | 5.1 | 22 | 41 | 31 | 0.25 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 7×0.25 | 7×0.25 | 24 | 5.3 | 5.8 | 32 | 59 | 35 | 0.25 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 12×0.25 | 12×0.25 | 24 | 6.7 | 7.3 | 51 | 96 | 44 | 0.25 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 25×0.25 | 25×0.25 | 24 | 9.5 | 10.3 | 98 | 184 | 62 | 0.25 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 2×0.34 | 2×0.34 | 22 | 4.6 | 5 | 19 | 36 | 30 | 0.34 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 4×0.34 | 4×0.34 | 22 | 5.2 | 5.6 | 28 | 49 | 34 | 0.34 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 8×0.34 | 8×0.34 | 22 | 6.5 | 7.1 | 47 | 86 | 43 | 0.34 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 12×0.34 | 12×0.34 | 22 | 7.5 | 8.1 | 66 | 120 | 49 | 0.34 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 2×0.5 | 2×0.5 | 20 | 5 | 5.4 | 24 | 42 | 32 | 0.50 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 4×0.5 | 4×0.5 | 20 | 5.6 | 6.1 | 36 | 61 | 37 | 0.50 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 7×0.5 | 7×0.5 | 20 | 6.7 | 7.3 | 56 | 95 | 44 | 0.50 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 12×0.5 | 12×0.5 | 20 | 8.6 | 9.4 | 89 | 158 | 56 | 0.50 mm² Screened LSZH Signal Configurations (500 V peak)
| LiHCH 2×0.75 | 2×0.75 | 18 | 5.4 | 5.9 | 30 | 52 | 35 | 0.75–1.5 mm² Screened LSZH Signal & Control Configurations
| LiHCH 4×0.75 | 4×0.75 | 18 | 6.2 | 6.7 | 47 | 79 | 40 | 0.75–1.5 mm² Screened LSZH Signal & Control Configurations
| LiHCH 7×0.75 | 7×0.75 | 18 | 7.5 | 8.1 | 77 | 126 | 49 | 0.75–1.5 mm² Screened LSZH Signal & Control Configurations
| LiHCH 4×1.0 | 4×1.0 | 17 | 6.6 | 7.2 | 59 | 96 | 43 | 0.75–1.5 mm² Screened LSZH Signal & Control Configurations
| LiHCH 4×1.5 | 4×1.5 | 16 | 7.5 | 8.1 | 82 | 129 | 49 | 0.75–1.5 mm² Screened LSZH Signal & Control Configurations
Dimensions and weights are typical values per DIN VDE 0812 / DIN 47100 · LSZH EMC. Minimum fixed bending radius shown is 6 × OD.

## Electrical & current ratings
LiHCH Screened LSZH Signal Cable – Electrical & current ratings (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lihch-screened-lszh-signal-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100 · LSZH EMC. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.14 | 26 | 138 | 2.0 | 1.5
0.25 | 24 | 79 | 4.0 | 3.0
0.34 | 22 | 57 | 5.0 | 4.0
0.5 | 20 | 39 | 9.0 | 6.0
0.75 | 18 | 26 | 12.0 | 10.0
1 | 17 | 19.5 | 15.0 | 13.0
1.5 | 16 | 13.3 | 23.0 | 18.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
LiHCH Screened LSZH Signal Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/lihch-screened-lszh-signal-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100 · LSZH EMC. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 350 / 500 V (0.14 mm²: 350 V · ≥0.25 mm²: 500 V)
Key data | EMC screen | ≥ 80 % CuSn (Tinned-copper wire braid screen)
Key data | Halogen-free | IEC 60754-1/2 (Zero halogen · pH ≥ 4.3 · ≤ 10 µS/mm)
Key data | Smoke density | IEC 61034-2 (≥ 60 % light transmittance in fire)
Key data | Bending radius | 6–15 × OD (6 × OD fixed · 15 × OD flexing)
Key data | Size range | 0.14–1.5 mm² (2 to 36 cores · DIN 47100 colours)
Electrical | Peak operating voltage | 350 V (0.14 mm²) · 500 V (≥ 0.25 mm²)
Electrical | AC test voltage (50 Hz) | 1200 V (0.14 mm²) · 1500 V (≥ 0.25 mm²) core/core & core/screen
Electrical | Mutual capacitance (800 Hz) | Approx. 115 nF/km (core/core) · approx. 155 nF/km (core/screen)
Electrical | Transfer impedance (30 MHz) | ≤ 250 mΩ/m via ≥ 80 % tinned-copper braid
Electrical | Insulation resistance | ≥ 200 MΩ·km at +20 °C
Thermal | Temperature, flexing | −5 °C to +70 °C
Thermal | Temperature, fixed | −30 °C to +80 °C
Thermal | Max. conductor temperature | +70 °C in motion · +80 °C fixed
Thermal | Short-circuit temperature | +150 °C max.
Mechanical | Min. bending radius, fixed | 6 × overall diameter
Mechanical | Min. bending radius, flexing | 15 × overall diameter
Mechanical | Screen coverage | ≥ 80 % optical coverage tinned-copper wire braid
Resistance | Halogen-free & non-corrosive | IEC 60754-1 / EN 60754-1 & IEC 60754-2 (pH ≥ 4.3, conductivity ≤ 10 µS/mm)
Resistance | Low smoke emission | IEC 61034-2 / EN 61034-2 (≥ 60 % light transmittance)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat. C bunched vertical flame test
Standards | Construction basis | DIN VDE 0812 & DIN VDE 0207-24 (HI2/HM2)
Standards | Core colour code | DIN 47100 (without green-yellow earth core)
Standards | Fire safety standards | IEC 60754-1/2, IEC 61034-2, IEC 60332-1-2 / 60332-3-24
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Pebble-grey (RAL 7032)
Identification | Core identification | DIN 47100 colour & bi-colour ring code
Identification | Sheath marking | TEBAOFLEX LiHCH [Size] HALOGEN-FREE EMC SCREENED DIN VDE 0812 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
LiHCH Screened LSZH Signal Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/lihch-screened-lszh-signal-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100 · LSZH EMC. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded copper conductor | Annealed bare copper strands to DIN VDE 0812 / IEC 60228 Class 5 | DIN VDE 0812 / IEC 60228
2 | Halogen-free LSZH core insulation (H) | Thermoplastic polyolefin compound Type HI2 / TI6 (DIN VDE 0207-24) colour-coded to DIN 47100 | DIN VDE 0207-24 · DIN 47100
3 | Halogen-free wrapping tape | Overlapped halogen-free polyester tape over the stranded core bundle | DIN VDE 0812
4 | Tinned-copper braid screen (C) | Close-woven tinned annealed copper wire braid with ≥ 80 % optical coverage for low transfer impedance | DIN VDE 0812 · EN 55011 EMC
5 | Halogen-free LSZH outer sheath (H) | Flame-retardant low-smoke zero-halogen compound Type HM2, pebble-grey RAL 7032 | DIN VDE 0207-24 HM2 · IEC 60754 / 61034
| LiHCH 0.14–0.34 mm² (2 to 36 cores) | Compact EMC-screened halogen-free sensor, encoder and instrumentation cables
| LiHCH 0.5–1.5 mm² (2 to 25 cores) | Screened LSZH analog 4–20 mA, damper actuator and PLC I/O cables
| LiHCH (TP) Twisted Pair Option | Available in twisted-pair construction (`n × 2 × mm²`) for low-crosstalk differential LSZH signals

## Quality and supply
LiHCH Screened LSZH Signal Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/lihch-screened-lszh-signal-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100 · LSZH EMC. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 1.5 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0812 / DIN 47100 · LSZH EMC (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0812 / DIN 47100 · LSZH EMC | Type approval
Standard / approval | DIN VDE 0812 / DIN 47100 · LSZH EMC
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX LiHCH [Size] HALOGEN-FREE EMC SCREENED DIN VDE 0812 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request