## Request a quote
Request a quotation for LiYCY (TP)
Application engineer · differential signal & encoder cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/liycy-tp-screened-twisted-pair-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
LiYCY (TP) Screened Twisted-Pair Cable – Dimensions & weights (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/liycy-tp-screened-twisted-pair-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| LiYCY (TP) 2×2×0.14 | 2×2×0.14 | 26 | 4.4 | 4.8 | 18 | 30 | 29 | n × 2 × 0.14 mm² Twisted-Pair Screened (350 V peak)
| LiYCY (TP) 3×2×0.14 | 3×2×0.14 | 26 | 4.8 | 5.2 | 23 | 38 | 31 | n × 2 × 0.14 mm² Twisted-Pair Screened (350 V peak)
| LiYCY (TP) 4×2×0.14 | 4×2×0.14 | 26 | 5.3 | 5.8 | 27 | 48 | 35 | n × 2 × 0.14 mm² Twisted-Pair Screened (350 V peak)
| LiYCY (TP) 8×2×0.14 | 8×2×0.14 | 26 | 6.7 | 7.3 | 49 | 81 | 44 | n × 2 × 0.14 mm² Twisted-Pair Screened (350 V peak)
| LiYCY (TP) 2×2×0.25 | 2×2×0.25 | 24 | 5.2 | 5.6 | 25 | 42 | 34 | n × 2 × 0.25 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 3×2×0.25 | 3×2×0.25 | 24 | 5.5 | 6 | 32 | 51 | 36 | n × 2 × 0.25 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 4×2×0.25 | 4×2×0.25 | 24 | 6.2 | 6.7 | 38 | 64 | 40 | n × 2 × 0.25 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 8×2×0.25 | 8×2×0.25 | 24 | 8.1 | 8.8 | 70 | 115 | 53 | n × 2 × 0.25 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 12×2×0.25 | 12×2×0.25 | 24 | 9.5 | 10.3 | 100 | 162 | 62 | n × 2 × 0.25 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 2×2×0.34 | 2×2×0.34 | 22 | 5.7 | 6.2 | 31 | 52 | 37 | n × 2 × 0.34 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 4×2×0.34 | 4×2×0.34 | 22 | 6.9 | 7.5 | 50 | 82 | 45 | n × 2 × 0.34 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 8×2×0.34 | 8×2×0.34 | 22 | 8.9 | 9.7 | 90 | 146 | 58 | n × 2 × 0.34 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 2×2×0.5 | 2×2×0.5 | 20 | 6.3 | 6.9 | 41 | 65 | 41 | n × 2 × 0.50 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 3×2×0.5 | 3×2×0.5 | 20 | 6.8 | 7.4 | 53 | 82 | 44 | n × 2 × 0.50 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 4×2×0.5 | 4×2×0.5 | 20 | 7.6 | 8.3 | 66 | 102 | 50 | n × 2 × 0.50 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 8×2×0.5 | 8×2×0.5 | 20 | 10.3 | 11.2 | 121 | 189 | 67 | n × 2 × 0.50 mm² Twisted-Pair Screened (500 V peak)
| LiYCY (TP) 2×2×0.75 | 2×2×0.75 | 18 | 7.1 | 7.7 | 54 | 84 | 46 | n × 2 × 0.75–1.0 mm² Twisted-Pair Screened
| LiYCY (TP) 4×2×0.75 | 4×2×0.75 | 18 | 8.5 | 9.2 | 89 | 134 | 55 | n × 2 × 0.75–1.0 mm² Twisted-Pair Screened
| LiYCY (TP) 8×2×0.75 | 8×2×0.75 | 18 | 11.2 | 12.2 | 168 | 248 | 73 | n × 2 × 0.75–1.0 mm² Twisted-Pair Screened
| LiYCY (TP) 2×2×1.0 | 2×2×1.0 | 17 | 7.5 | 8.2 | 68 | 102 | 49 | n × 2 × 0.75–1.0 mm² Twisted-Pair Screened
| LiYCY (TP) 4×2×1.0 | 4×2×1.0 | 17 | 9.1 | 9.9 | 116 | 168 | 59 | n × 2 × 0.75–1.0 mm² Twisted-Pair Screened
Dimensions and weights are typical values per DIN VDE 0812 / DIN 47100. Minimum fixed bending radius shown is 6 × OD.

## Electrical & current ratings
LiYCY (TP) Screened Twisted-Pair Cable – Electrical & current ratings (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/liycy-tp-screened-twisted-pair-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.14 | 26 | 138 | 2.0 | 1.5
0.25 | 24 | 79 | 4.0 | 3.0
0.34 | 22 | 57 | 5.0 | 4.0
0.5 | 20 | 39 | 9.0 | 6.0
0.75 | 18 | 26 | 12.0 | 10.0
1 | 17 | 19.5 | 15.0 | 13.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
LiYCY (TP) Screened Twisted-Pair Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/liycy-tp-screened-twisted-pair-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 350 / 500 V (0.14 mm²: 350 V · ≥0.25 mm²: 500 V)
Key data | Core geometry | Twisted pairs (2×2 to 25×2 pairs · low crosstalk)
Key data | EMC screen | ≥ 80 % CuSn (Overall tinned-copper braid screen)
Key data | Temp. flexing | −5…+70 °C (−30…+80 °C fixed installation)
Key data | Bending radius | 6–15 × OD (6 × OD fixed · 15 × OD flexing)
Key data | Size range | 0.14–1.0 mm² (2×2 to 25×2 pairs · DIN 47100)
Electrical | Peak operating voltage | 350 V (0.14 mm²) · 500 V (≥ 0.25 mm²)
Electrical | AC test voltage (50 Hz) | 1200 V (0.14 mm²) · 1500 V (≥ 0.25 mm²) core/core & core/screen
Electrical | Mutual capacitance (800 Hz) | Approx. 120 nF/km (core/core) · approx. 160 nF/km (core/screen)
Electrical | Near-end crosstalk (NEXT) | ≥ 50 dB attenuation at 100 kHz via balanced pair lay
Electrical | Inductance | Approx. 0.65 mH/km
Electrical | Insulation resistance | ≥ 200 MΩ·km at +20 °C
Thermal | Temperature, flexing | −5 °C to +70 °C
Thermal | Temperature, fixed | −30 °C to +80 °C
Thermal | Max. conductor temperature | +70 °C in motion · +80 °C fixed
Thermal | Short-circuit temperature | +150 °C max.
Mechanical | Min. bending radius, fixed | 6 × overall diameter
Mechanical | Min. bending radius, flexing | 15 × overall diameter
Mechanical | Pair construction | 2 cores twisted into a pair (TP); pairs stranded in concentric layers
Mechanical | Screen coverage | ≥ 80 % optical coverage tinned-copper wire braid
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 self-extinguishing · CPR Eca
Resistance | EMC & crosstalk | Balanced pair lay rejects differential magnetic pickup + braid blocks RF interference
Standards | Construction basis | DIN VDE 0812
Standards | Pair colour code | DIN 47100 pair sequence (Pair 1: white/brown, Pair 2: green/yellow, Pair 3: grey/pink…)
Standards | Compounds | DIN VDE 0207-4 Type YI2 (core) & DIN VDE 0207-5 Type YM2 (sheath)
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Pebble-grey (RAL 7032)
Identification | Pair identification | DIN 47100 colour & bi-colour ring code paired in sequence
Identification | Sheath marking | TEBAOFLEX LiYCY (TP) [n×2×mm²] DIN VDE 0812 / DIN 47100 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
LiYCY (TP) Screened Twisted-Pair Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/liycy-tp-screened-twisted-pair-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded copper conductor | Annealed bare copper strands to DIN VDE 0812 / IEC 60228 Class 5 | DIN VDE 0812 / IEC 60228
2 | Thin-wall PVC core insulation | Semi-rigid PVC compound Type YI2 (DIN VDE 0207-4), pair colour-coded to DIN 47100 | DIN VDE 0207-4 YI2 · DIN 47100
3 | Twisted-pair stranding (TP) | Insulated cores twisted into balanced pairs with short lay length and stranded in concentric layers | DIN VDE 0812
4 | PET tape + tinned-copper braid (C) | Overlapped polyester tape plus ≥ 80 % optical coverage tinned-copper wire braid screen | DIN VDE 0812 · EN 55011 EMC
5 | PVC outer sheath | Flame-retardant polyvinyl chloride compound Type YM2, pebble-grey RAL 7032 | DIN VDE 0207-5 YM2 · IEC 60332-1-2
| LiYCY (TP) 0.14–0.25 mm² (2×2 to 25×2) | High-density twisted-pair encoder, load-cell and serial interface cables
| LiYCY (TP) 0.34–1.0 mm² (2×2 to 16×2) | Low-drop twisted-pair analog 4–20 mA, valve feedback and process telemetry cables

## Quality and supply
LiYCY (TP) Screened Twisted-Pair Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/liycy-tp-screened-twisted-pair-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0812 / DIN 47100. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 1.5 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0812 / DIN 47100 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0812 / DIN 47100 | Type approval
Standard / approval | DIN VDE 0812 / DIN 47100
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX LiYCY (TP) [n×2×mm²] DIN VDE 0812 / DIN 47100 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request