## Request a quote
Request a quotation for Liquid-Cooled High-Power DC Charging Cable
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/liquid-cooled-high-power-dc-charging-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Liquid-Cooled High-Power DC Charging Cable – Current rating, dimensions & cooling (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/liquid-cooled-high-power-dc-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62893-4-2 / UL 2263 / EN 50620. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | DC power + PE + control | Outer Ø mm | Dry weight kg/m | Cont. DC A | Coolant flow L/min | Series
| HPC-LC 2×35+16+CP (400A) | 2×35 mm² DC + 16PE + 6×0.5C · 1000V | 28.8 | 1.42 | 400 | 1.8 | 1000–1500 V DC Liquid-Cooled EV Fast-Charging Cables
| HPC-LC 2×50+25+CP (500A) | 2×50 mm² DC + 25PE + 6×0.5C · 1000V | 30.8 | 1.75 | 500 | 2.2 | 1000–1500 V DC Liquid-Cooled EV Fast-Charging Cables
| HPC-LC 2×70+25+CP (650A) | 2×70 mm² DC + 25PE + 8×0.5C · 1200V | 33.2 | 2.15 | 650 | 2.8 | 1000–1500 V DC Liquid-Cooled EV Fast-Charging Cables
| MCS-LC 2×95+35+CP (850A) | 2×95 mm² DC + 35PE + 8×0.75C · 1500V | 35.8 | 2.68 | 850 | 3.5 | 1000–1500 V DC Liquid-Cooled EV Fast-Charging Cables
Continuous DC current ratings assume +25 °C coolant inlet temperature and +40 °C ambient air per IEC 62893-4-2.

## Technical data
Liquid-Cooled High-Power DC Charging Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/liquid-cooled-high-power-dc-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62893-4-2 / UL 2263 / EN 50620. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | IEC 62893-4-2 (& UL 2263 EV Charging)
Key data | DC voltage | 1,000 / 1,500 V (CCS1 / CCS2 / NACS / MCS)
Key data | Continuous current | 500 to 850 A DC (Up to 1,000 A boost peak)
Key data | DC conductor | 2 × 35–95 mm² (Replaces uncooled 2×185 mm²)
Key data | Coolant media | Water-Glycol/Oil (6–12 bar burst pressure tube)
Key data | Outer diameter | 28.5 to 36.0 mm (Easy single-hand EV handling)
Electrical | Rated DC power voltage | 1,000 V DC / 1,500 V DC (control cores: 30–60 V DC)
Electrical | Continuous DC current | 500 A (2×50 mm²) · 650 A (2×70 mm²) · 850 A (2×95 mm² @ 2.5 L/min)
Electrical | Dielectric test voltage | 3,500–5,000 V AC on DC power cores · 1,000 V AC on control cores
Electrical | Pilot / PLC impedance | Shielded twisted pair supports HomePlug GreenPHY (ISO 15118)
Thermal | Ambient operating temp. | -40 °C to +60 °C (surface touch temp kept ≤ +50 °C per IEC 61851)
Thermal | Max. conductor / coolant temp. | +90 °C max core temp (monitored by dual PT1000 / NTC loops)
Thermal | Heat dissipation capacity | Removes 150 to 320 W/m of I²R Joule heating via 2–4 L/min chiller
Mechanical | Nominal outer diameter | 29.5 mm (500 A) · 32.8 mm (650 A) · 35.8 mm (850 A MCS)
Mechanical | Min. bend radius | 5 × OD to 6 × OD (without coolant flow restriction < 90 %)
Mechanical | Flexing & torsion life | ≥ 50,000 bending cycles & ±180°/m torsion per IEC 62893-4-2
Resistance | Vehicle wheel crush test | Passes 5,000 N / 11,000 N vehicle drive-over without tube leak
Resistance | Coolant burst pressure | Working pressure 2–5 bar · Burst pressure ≥ 15 bar @ +85 °C
Resistance | Weather, oil & halogen-free | UV, gasoline, diesel, de-icing salt resistant & IEC 60754-1 LSZH
Standards | Liquid-cooled EV cable std | IEC 62893-4-2 & UL 2263 (EV Cable with Thermal Management)
Standards | System safety standard | IEC 61851-23 & SAE J1772 / J3400 / CharIN MCS
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Outer sheath | Matte Black E-TPU with contrasting Orange/Blue inner wear-indicator layer
Identification | Customs tariff (HS) | 8544.4993
Identification | Core identification | DC+ (Red/Brown), DC− (Black/Blue), PE (GNYE) + colour-coded pilot/sensor

## Construction
Liquid-Cooled High-Power DC Charging Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/liquid-cooled-high-power-dc-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62893-4-2 / UL 2263 / EN 50620. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 2 × Liquid-cooled Class 6 copper DC+ & DC− cores + PE | 2 × 35, 50, 70 or 95 mm² Class 6 extra-fine bare/tinned copper stranded around/within flexible coolant micro-ducts + 16–25 mm² PE earth conductor
2 | Closed-loop coolant supply & return tubing | Kink-resistant fluoropolymer (FEP/PFA), cross-linked PE or peroxide-cured elastomer coolant conduits (working pressure 2–5 bar, burst ≥ 15 bar)
3 | 1,000–1,500 V DC TPE-E / EPR power core insulation | High-dielectric halogen-free elastomer/TPE insulation on DC+, DC− and PE cores
4 | Shielded CP / PP / PLC control + PT1000 sensor pairs | 4 to 8 × 0.50–0.75 mm² tinned copper control & temperature-interlock cores with tinned copper braid shield (≥ 85 %)
5 | Dual-layer wear-indicating E-TPU (PUR) outer sheath | Co-extruded Matte Black outer / Coloured inner wear-indicator Polyether Polyurethane (E-TPU) jacket
| HPC-LC-500A (2×35 / 2×50 mm² · 1000 V DC) | Slim 29.5–31.5 mm OD water-glycol or oil-cooled cable for 350–500 kW CCS1 / CCS2 / NACS passenger EV chargers
| HPC-LC-650A (2×70 mm² · 1200 V DC) | 650 A continuous (800 A boost) liquid-cooled charging cable for high-utilization highway fleet plazas
| MCS-LC-850A (2×95 mm² · 1500 V DC Megawatt) | 850 A continuous (1,000+ A peak) 1,500 V DC liquid-cooled cable for commercial truck Megawatt Charging System (MCS)

## Quality and supply
Liquid-Cooled High-Power DC Charging Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/liquid-cooled-high-power-dc-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62893-4-2 / UL 2263 / EN 50620. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 5.0 kV AC dielectric, DC resistance & 10 bar hydraulic pressure test — Zero electrical breakdown and zero coolant tube pressure drop over 30 min | Every manufactured cable length
Type test | 50,000-cycle flex + ±180°/m torsion under internal coolant pressure — No copper strand break, < 10 % flow restriction and zero leakage | Type qualification
Type test | Vehicle drive-over crush (11 kN) & -40 °C cold impact test — Zero tube rupture or insulation short after tire crush | Type qualification
Standard / approval | IEC 62893-4-2 Compliant
Standard / approval | UL 2263 EV Charging
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX LIQUID-COOLED HPC DC CHARGING CABLE 1000V/1500V IEC 62893-4-2
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP