## Request a quote
Request a quotation for MC-HL Instrumentation
Application engineer · NEC & offshore hazardous-location cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mc-hl-metal-clad-instrumentation-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MC-HL Instrumentation Metal-Clad Instrumentation Cable – Dimensions & weights (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Articles 330, 501.10(A) & 505. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Shielding | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| MC-HL-INST 1P×18AWG OS | 1 Pair × 18 AWG + GND | OS | 13.2 | 28 | 178 | 132 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 2P×18AWG IS/OS | 2 Pairs × 18 AWG + GND | IS+OS | 16.4 | 52 | 265 | 164 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 4P×18AWG IS/OS | 4 Pairs × 18 AWG + GND | IS+OS | 19.2 | 96 | 378 | 192 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 8P×18AWG IS/OS | 8 Pairs × 18 AWG + GND | IS+OS | 24.1 | 182 | 610 | 241 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 12P×18AWG IS/OS | 12 Pairs × 18 AWG + GND | IS+OS | 28.2 | 268 | 845 | 282 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 24P×18AWG IS/OS | 24 Pairs × 18 AWG + GND | IS+OS | 37.6 | 515 | 1490 | 376 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 1P×16AWG OS | 1 Pair × 16 AWG + GND | OS | 14 | 42 | 202 | 140 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 2P×16AWG IS/OS | 2 Pairs × 16 AWG + GND | IS+OS | 17.6 | 78 | 308 | 176 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 4P×16AWG IS/OS | 4 Pairs × 16 AWG + GND | IS+OS | 20.8 | 146 | 452 | 208 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 8P×16AWG IS/OS | 8 Pairs × 16 AWG + GND | IS+OS | 26.2 | 278 | 735 | 262 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 12P×16AWG IS/OS | 12 Pairs × 16 AWG + GND | IS+OS | 30.8 | 410 | 1020 | 308 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 24P×16AWG IS/OS | 24 Pairs × 16 AWG + GND | IS+OS | 41.2 | 795 | 1810 | 412 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 1P×14AWG OS | 1 Pair × 14 AWG + GND | OS | 15.2 | 64 | 245 | 152 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 4P×14AWG IS/OS | 4 Pairs × 14 AWG + GND | IS+OS | 22.8 | 224 | 575 | 228 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type MC-HL
| MC-HL-INST 8P×14AWG IS/OS | 8 Pairs × 14 AWG + GND | IS+OS | 29 | 428 | 945 | 290 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type MC-HL
Terminate with UL 2225 listed MC-HL potted/elastomeric barrier connectors (e.g. TMCX) in Class I Division 1 enclosures.

## Electrical parameters by AWG ga
MC-HL Instrumentation Metal-Clad Instrumentation Cable – Electrical parameters by AWG gauge (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Articles 330, 501.10(A) & 505. Values for your order are confirmed in the quotation.
AWG size (metric) | Equip. ground wire AWG | Max. DC R @ 20 °C Ω/km | Nom. C (core/core) pF/m | AC test V rms
18 AWG (0.82 mm² · 7×26) | 18 AWG | 21.4 | 82 | 2000
16 AWG (1.31 mm² · 7×24) | 16 AWG | 13.7 | 88 | 2000
14 AWG (2.08 mm² · 7×22) | 14 AWG | 8.6 | 94 | 2000
12 AWG (3.31 mm²) and multi-triad (1T–12T) MC-HL instrumentation cables are also available.

## Technical data
MC-HL Instrumentation Metal-Clad Instrumentation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Articles 330, 501.10(A) & 505. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600 V rms (UL 2225 MC-HL & UL 1569 MC)
Key data | Metallic sheath | CWCMC Aluminium (continuously welded corrugated)
Key data | Hazardous area | Class I Div 1/2 (Class II & III Div 1 · Zone 1/2)
Key data | Temperature | −40…+90 °C (wet & dry XHHW-2 · +250 °C SC)
Key data | Shielding | OS or IS+OS (100 % Al/PET foil + drain wires)
Key data | Bend radius | 10 × OD (fixed · 12 × OD during pulling)
Electrical | Rated voltage | 600 V rms (Type MC-HL) · 300 V rms (Type ITC-HL)
Electrical | Dielectric test voltage | 2000 V AC rms for 5 min
Electrical | Insulation resistance | ≥ 2000 MΩ·km at +20 °C
Electrical | Shielding effectiveness | Dual-layer: internal Al/PET foil + 360° solid welded Al tube
Thermal | Operating temperature | −40 °C to +90 °C (wet or dry)
Thermal | Short-circuit conductor temperature | +250 °C (XHHW-2 thermoset XLPE)
Mechanical | UL 2225 crush & impact rating | ≥ 2,000 lbf (8.9 kN) crush · ≥ 50 ft-lbf (68 J) impact
Mechanical | Sheath pressure tightness | 100 % air-pressure & weld-integrity tested continuous tube
Mechanical | Min. bending radius | 10 × OD (fixed) · 12 × OD (pulling)
Resistance | Flame test ratings | UL 1685 · IEEE 1202 (70,000 BTU/hr) · IEC 60332-3-22 · CSA FT4
Resistance | Chemical & hydrocarbon barrier | 100 % impervious welded metallic sheath (zero permeation)
Standards | UL standards | UL 2225 (Type MC-HL / ITC-HL) & UL 1569 (Type MC)
Standards | NEC & Coast Guard | NEC Art. 330, 501.10(A)(1)(c), 502, 503, 505 · USCG / API RP 14F
Identification | Core identification | Black / White numbered pairs + Green equipment ground
Identification | Outer jacket colour | Black (or Blue for Ex-i)
Identification | Customs tariff (HS) | 8544.49

## Construction
MC-HL Instrumentation Metal-Clad Instrumentation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Articles 330, 501.10(A) & 505. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded copper conductors + equipment ground | 18 AWG, 16 AWG, 14 AWG or 12 AWG Class B stranded copper pairs/triads plus UL 1569/2225 equipment grounding conductor
2 | 600 V 90 °C XHHW-2 cross-linked polyethylene | Thermoset XLPE (UL 44 XHHW-2) colour-coded Black/White numbered pairs (or Black/White/Red triads)
3 | Individual & overall 100 % Al/PET shields | Isolated Aluminium/PET pair shields (IS) + overall Al/PET shield (OS) with tinned copper drain wires
4 | Polymeric core binder tape | Helical thermal & mechanical barrier tape over the shielded core bundle
5 | Continuously welded corrugated aluminium sheath | Seamless longitudinal TIG/laser-welded and annularly corrugated aluminium tube (316L stainless steel or copper-alloy optional)
6 | Sunlight & Oil Resistant PVC or LSZH jacket | Flame-retardant PVC (or CPE / LSZH) extruded over the corrugated aluminium armour, Black or Ex-i Blue
| MC-HL OS (Single Pair / Triad) | 1P or 1T (18–12 AWG) with overall Al/PET shield and welded corrugated aluminium armour
| MC-HL IS/OS (Multi-Pair Trunk) | 2P to 36P with individual & overall Al/PET shields and welded corrugated aluminium armour
| MC-HL 316L Stainless / LSZH | Continuously welded corrugated 316L stainless steel sheath with halogen-free LSZH jacket

## Quality and supply
MC-HL Instrumentation Metal-Clad Instrumentation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-instrumentation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Articles 330, 501.10(A) & 505. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Continuous weld-seam eddy-current & air-pressure leak test — 100 % gas/vapour-tight corrugated aluminium sheath along entire length | Every manufactured reel
Routine test | 2000 V AC dielectric test — 2.0 kV rms AC for 5 min without breakdown | Every manufactured reel
Sample test | UL 2225 2,000 lbf crush & 50 ft-lbf impact test — Pass hazardous-location crush and impact tests | UL follow-up audit
Standard / approval | UL 2225 & UL 1569 Listed Type MC-HL (600 V)
Standard / approval | NEC Art. 330, 501, 502, 503 & 505 Div 1 / Zone 1
Standard / approval | API RP 14F, USCG & ABS Offshore
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX <size> E-FILE (UL) TYPE MC-HL / ITC-HL 600V XHHW-2 90C SUN RES OIL RES I/II DIR BUR FT4
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP