## Request a quote
Request a quotation for MC-HL Power
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mc-hl-metal-clad-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MC-HL Power Metal-Clad Power Cable – Dimensions & masses (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Art. 330 & 501. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | 3 Phase + 3 Split Ground | Ground AWG / NEC 90°C A | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| MC-HL 3C 14 AWG | 3C × 14 AWG + 3G | 3×18 AWG Gd · 25 A | 14.2 | 68 | 235 | 99.4 | MC-HL Power size schedule
| MC-HL 3C 12 AWG | 3C × 12 AWG + 3G | 3×16 AWG Gd · 30 A | 15.2 | 108 | 285 | 106.4 | MC-HL Power size schedule
| MC-HL 3C 10 AWG | 3C × 10 AWG + 3G | 3×14 AWG Gd · 40 A | 16.8 | 172 | 370 | 117.6 | MC-HL Power size schedule
| MC-HL 3C 8 AWG | 3C × 8 AWG + 3G | 3×14 AWG Gd · 55 A | 19.6 | 248 | 510 | 137.2 | MC-HL Power size schedule
| MC-HL 3C 6 AWG | 3C × 6 AWG + 3G | 3×12 AWG Gd · 75 A | 22.1 | 395 | 710 | 154.7 | MC-HL Power size schedule
| MC-HL 3C 4 AWG | 3C × 4 AWG + 3G | 3×12 AWG Gd · 95 A | 25.4 | 602 | 990 | 177.8 | MC-HL Power size schedule
| MC-HL 3C 2 AWG | 3C × 2 AWG + 3G | 3×10 AWG Gd · 130 A | 28.7 | 955 | 1430 | 200.9 | MC-HL Power size schedule
| MC-HL 3C 1/0 AWG | 3C × 1/0 AWG + 3G | 3×10 AWG Gd · 170 A | 33.8 | 1455 | 2060 | 236.6 | MC-HL Power size schedule
| MC-HL 3C 2/0 AWG | 3C × 2/0 AWG + 3G | 3×8 AWG Gd · 195 A | 36.6 | 1875 | 2550 | 256.2 | MC-HL Power size schedule
| MC-HL 3C 4/0 AWG | 3C × 4/0 AWG + 3G | 3×6 AWG Gd · 260 A | 42.4 | 2975 | 3890 | 296.8 | MC-HL Power size schedule
| MC-HL 3C 250 MCM | 3C × 250 MCM + 3G | 3×6 AWG Gd · 290 A | 46.2 | 3415 | 4460 | 323.4 | MC-HL Power size schedule
| MC-HL 3C 350 MCM | 3C × 350 MCM + 3G | 3×4 AWG Gd · 350 A | 51.6 | 4800 | 6050 | 361.2 | MC-HL Power size schedule
| MC-HL 3C 500 MCM | 3C × 500 MCM + 3G | 3×4 AWG Gd · 430 A | 58.4 | 6600 | 8180 | 408.8 | MC-HL Power size schedule
Dimensions and tolerances conform to UL 2225 / UL 1569 / NEC Art. 330 & 501.

## Electrical data
MC-HL Power Metal-Clad Power Cable – Electrical data (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Art. 330 & 501. Values for your order are confirmed in the quotation.
3 Phase + 3 Split Ground | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
3C × 14 AWG + 3G | 8.45 | 25 | 20
3C × 12 AWG + 3G | 5.31 | 30 | 24
3C × 10 AWG + 3G | 3.34 | 40 | 32
3C × 8 AWG + 3G | 2.1 | 55 | 44
3C × 6 AWG + 3G | 1.32 | 75 | 60
3C × 4 AWG + 3G | 0.83 | 95 | 76
3C × 2 AWG + 3G | 0.52 | 130 | 104
3C × 1/0 AWG + 3G | 0.328 | 170 | 136
3C × 2/0 AWG + 3G | 0.261 | 195 | 156
3C × 4/0 AWG + 3G | 0.164 | 260 | 208
3C × 250 MCM + 3G | 0.139 | 290 | 232
3C × 350 MCM + 3G | 0.099 | 350 | 280
3C × 500 MCM + 3G | 0.07 | 430 | 344
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
MC-HL Power Metal-Clad Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Art. 330 & 501. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage ratings | 600 V to 15 kV (600 V, 1/2 kV VFD, 5 kV & 15 kV)
Key data | Hazardous rating | Class I Div 1 & (NEC Art. 501 / 505 Zone 1 & 2)
Key data | Metallic sheath | Continuously wel (Impervious corrugated CWCMC tube)
Key data | Grounding / VFD | 3 symmetrical gr (Low common-mode VFD impedance)
Key data | Core insulation | XHHW-2 XLPE or E (90 °C wet/dry (+130 °C overload))
Key data | Operating temp | -40 to +90 °C (Offshore, refinery & LNG rated)
Electrical | Rated voltage | 600 V / 1,000 V / 2,000 V VFD (plus 5 kV & 15 kV MV series)
Electrical | Dielectric test & sheath pressure test | 3.5 kV AC dielectric + 100 % continuous pneumatic/eddy-current weld integrity test
Thermal | Conductor temperature rating | +90 °C wet or dry · +130 °C emergency overload · +250 °C short-circuit
Thermal | Installation & operating temperature | -40 °C cold impact & cold bend to +90 °C continuous
Mechanical | Minimum bending radius | 7 × OD (fixed training) · 12 × OD (pulling)
Mechanical | Crush & impact resistance | Passes UL 2225 severe Class I Div 1 crush & impact tests (comparable to rigid steel conduit)
Resistance | Imperviousness to gas, vapour & liquids | Seamless welded aluminum tube blocks hydrocarbon migration and water ingress
Resistance | Flame & oil resistance | UL 1685 / IEEE 1202 / CSA FT4 70,000 BTU/hr tray flame · Oil Resistant I & II
Standards | Governing standards | UL 2225, UL 1569, UL 1277, CSA C22.2 No. 123 & NEC Articles 330, 501, 505
Standards | Marine & offshore approvals | US Coast Guard (USCG), ABS & IEEE 45 / API RP 14F compliant
Identification | Phase core identification | Black, White, Red (or numbered / ICEA Method 1/4) + 3 bare grounds
Identification | Outer jacket colour | Black (or HL/VFD stripe identification)

## Construction
MC-HL Power Metal-Clad Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Art. 330 & 501. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 × stranded copper phase conductors | Compressed concentric stranded annealed bare or tinned copper (14 AWG to 750 MCM) per UL 1569 / UL 44 | UL 1569
2 | XHHW-2 XLPE (or EPR) 90 °C dielectric | Thermoset cross-linked polyethylene (XHHW-2) or ethylene-propylene rubber (EPR) rated +90 °C wet/dry | UL 44
3 | 3 × symmetrical bare copper grounds | Three bare copper ground wires nestled at 120° intervals in the core interstices for balanced fault & VFD common-mode return | UL 2225
4 | Continuously welded corrugated Al (CWCMC) | Seamless seam-welded and corrugated aluminum tube forming a 100 % gas-, vapour- and liquid-impervious metallic barrier | UL 2225
5 | Oil, chemical & UV PVC / CPE outer jacket | -40 °C flame-retardant (IEEE 1202 / FT4), Oil Resistant I & II black polymeric outer sheath | UL 2225
| 600 V / 1000 V MC-HL Power & VFD Cable (14 AWG to 750 MCM — 3 Phase + 3 Symmetrical Grounds) | XHHW-2 XLPE insulated 3-phase power and inverter feeder cable for Class I Div 1 & 2 hazardous locations.
| 2.4 kV / 5 kV / 15 kV MV MC-HL (EPR Insulated, Shielded) | Medium-voltage copper-tape-shielded EPR + welded corrugated aluminum sheath MC-HL for offshore and refinery MV distribution.

## Quality and supply
MC-HL Power Metal-Clad Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mc-hl-metal-clad-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2225 / UL 1569 / NEC Art. 330 & 501. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric + 100 % eddy-current & pressure weld test — Zero electrical breakdown; 100 % gas-tight aluminum weld seam | 100 % of reels
Sample test | UL 2225 severe crush/impact & -40 °C cold impact test — Passes Class I Div 1 mechanical crush & arctic impact | Every batch
Type test | IEEE 1202 / UL 1685 70,000 BTU/hr flame & gas-tightness test — UL 2225 Listed Type MC-HL | Type qualification
Standard / approval | UL 2225 Listed Type MC-HL
Standard / approval | UL 1569 Type MC & UL 1277
Standard / approval | NEC Class I, II, III Div 1 & 2 (Zone 1 & 2)
Standard / approval | USCG & ABS Offshore Approved
Standard / approval | IEEE 1202 / CSA FT4
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) TYPE MC-HL [3/C AWG + 3 SYM GND] XHHW-2 600V/1000V VFD CWCMC -40C OIL RES II SUN RES IEEE 1202 FT4 [lot/ft]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP