## Request a quote
Request a quotation for MGM 109 Type 1012 / 1013 / 1014
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for MGM 109 Type 1012 / 1013 / 1014.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mgm-109-single-armoured-lv-feeder-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MGM 109 Type 1012 / 1013 / 1014 Single-Armoured LV Feeder Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-single-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| MGM 109 Type 1012 2C × 4.0 mm² SWA | 2 × 4.0 mm² (Type 1012) | 4.0 mm² | 16.4 | 77 | 490 | 131 | Standard MGM 109 Type 1012 / 1013 / 1014 configurations
| MGM 109 Type 1013 3C × 6.0 mm² SWA | 3 × 6.0 mm² (Type 1013) | 6.0 mm² | 18.8 | 173 | 680 | 150 | Standard MGM 109 Type 1012 / 1013 / 1014 configurations
| MGM 109 Type 1013 3C × 16 mm² SWA | 3 × 16 mm² (Type 1013) | 16.0 mm² | 23.6 | 461 | 1180 | 189 | Standard MGM 109 Type 1012 / 1013 / 1014 configurations
| MGM 109 Type 1013 3C × 50 mm² SWA | 3 × 50 mm² (Type 1013) | 50.0 mm² | 33.4 | 1440 | 2480 | 267 | Standard MGM 109 Type 1012 / 1013 / 1014 configurations
| MGM 109 Type 1013 3C × 95 mm² SWA (Cu/GSW) | 3 × 95 mm² (Type 1013) | 95.0 mm² | 42.8 | 3120 | 4380 | 342 | Standard MGM 109 Type 1012 / 1013 / 1014 configurations
| MGM 109 Type 1014 4C × 35 mm² SWA | 4 × 35 mm² (Type 1014) | 35.0 mm² | 32.6 | 1344 | 2360 | 261 | Standard MGM 109 Type 1012 / 1013 / 1014 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA).

## Electrical & ampacity
MGM 109 Type 1012 / 1013 / 1014 Single-Armoured LV Feeder Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-single-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
2 × 4.0 mm² (Type 1012) | 4.7 | 40 | 36 | 0.57 | 11.2 | 3500
3 × 6.0 mm² (Type 1013) | 3.11 | 51 | 46 | 0.86 | 6.8 | 3500
3 × 16 mm² (Type 1013) | 1.16 | 94 | 85 | 2.29 | 2.5 | 3500
3 × 50 mm² (Type 1013) | 0.391 | 185 | 166 | 7.15 | 0.82 | 3500
3 × 95 mm² (Type 1013) | 0.195 | 280 | 252 | 13.59 | 0.43 | 3500
4 × 35 mm² (Type 1014) | 0.529 | 152 | 137 | 5.01 | 1.15 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA).

## Technical data
MGM 109 Type 1012 / 1013 / 1014 Single-Armoured LV Feeder Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-single-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Specification | MGM 109 / BS (Type 1012 (2C) · 1013 (3C) · 1014 (4C))
Key data | Rated voltage | 640/1100 V AC (3.5 kV AC / 5 min dielectric test)
Key data | Armouring | Single Wire (Galvanized steel (+ Cu wires ≥ 75 %))
Key data | Earth conductance | ≥ 75 % of Phase (Metallic armour conductance ratio)
Key data | Insulation | Type GP4 EPR (90 °C cross-linked rubber BS 7655)
Key data | Outer sheath | Mining FR-PVC (Heavy-duty flame-retardant Black PVC)
Electrical | Rated voltage U0/U | 640/1100 V AC
Electrical | AC dielectric test voltage | 3,500 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Metallic armour conductance | ≥ 75 % of the conductance of one phase
Thermal | Operating temperature range | -15 °C to +90 °C (fixed installation)
Thermal | Minimum installation temp. | 0 °C
Mechanical | Min. bending radius | 8 × overall diameter (D) for SWA mining
Mechanical | Impact & crush protection | Single layer galvanized steel round wire
Resistance | Flame retardance | BS EN 60332-1-2 & British Coal underground
Resistance | Oil, water & chemical resistance | Resistant to mine water, hydraulic oil, and
Standards | Primary specification | British Coal Specification MGM 109 (Types
Standards | Material standards | BS EN 60228 · BS 7655-1.2 (GP4 EPR) · BS EN
Identification | Core identification | 2C: Brown/Blue · 3C: Brown/Black/Grey · 4C
Identification | Outer sheath colour | Black embossed 'MGM 109 TYPE 1012/1013/1014

## Construction
MGM 109 Type 1012 / 1013 / 1014 Single-Armoured LV Feeder Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-single-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper conductor | BS EN 60228 Class 2 circular stranded tinned annealed copper (2.5 to 185 mm²) | MGM 109 / BS EN 60228
2 | Type GP4 EPR rubber insulation (90 °C) | Cross-linked ethylene-propylene elastomer Type GP4 per BS 7655-1.2 | MGM 109 / BS 7655-1.2
3 | Extruded PVC inner bedding | Flame-retardant extruded PVC bedding over laid-up cores | MGM 109
4 | Single Wire Armour (SWA ≥ 75 % | Single helical layer of galvanized steel wires (with tinned copper wires on larger sizes | MGM 109 / BS 6708
5 | Mining flame-retardant PVC outer sheath | Heavy-duty abrasion- and flame-retardant PVC Type TM1/Type 9 outer sheath, Black | MGM 109 / BS 7655
| MGM 109 Type 1012 (2-Core × 2.5 to 35 mm²) | 640/1100 V 2-core single-wire-armoured lighting and auxiliary control power feeder.
| MGM 109 Type 1013 (3-Core) & Type 1014 (4-Core × 2.5 to 185 mm²) | 640/1100 V 3-core and 4-core single-wire-armoured roadway power distribution cables.

## Quality and supply
MGM 109 Type 1012 / 1013 / 1014 Single-Armoured LV Feeder Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-single-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 1012 / 1013 / 1014 LV SWA). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric & insulation resistance — 3,500 V AC for 5 min per MGM 109 / BS 6708 | 100 % of drums
Routine test | Phase & SWA armour DC resistance ratio — Armour conductance ≥ 75 % of largest phase conductor | 100 % of drums
Sample test | GP4 EPR hot-set & galvanizing coat weight — BS 7655-1.2 EPR & BS EN 10257-1 SWA wire tests | Per production batch
Type test | Underground mining flame & impact test — Pass MGM 109 / BS 6708 flame and mechanical crush checks | Type approval
Standard / approval | British Coal MGM 109
Standard / approval | BS 6708
Standard / approval | CE / UKCA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MGM 109 TYPE 1012 / 1013 / 1014
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP