## Request a quote
Request a quotation for MGM 109 Type 1023 / 1024
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for MGM 109 Type 1023 / 1024.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mgm-109-double-armoured-lv-feeder-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MGM 109 Type 1023 / 1024 Double-Armoured LV Feeder Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-double-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| MGM 109 Type 1024 4C × 16 mm² 640/1100V DWA | 4 × 16 mm² (Type 1024) | 16.0 mm² | 31.2 | 680 | 2480 | 374 | Standard MGM 109 Type 1023 / 1024 configurations
| MGM 109 Type 1023 3C × 25 mm² 640/1100V DWA | 3 × 25 mm² (Type 1023) | 25.0 mm² | 32.8 | 820 | 2760 | 394 | Standard MGM 109 Type 1023 / 1024 configurations
| MGM 109 Type 1023 3C × 50 mm² 640/1100V DWA | 3 × 50 mm² (Type 1023) | 50.0 mm² | 38.6 | 1610 | 3940 | 463 | Standard MGM 109 Type 1023 / 1024 configurations
| MGM 109 Type 1023 3C × 95 mm² 640/1100V DWA | 3 × 95 mm² (Type 1023) | 95.0 mm² | 47.4 | 3080 | 6120 | 569 | Standard MGM 109 Type 1023 / 1024 configurations
| MGM 109 Type 1023 3C × 120 mm² 640/1100V DWA | 3 × 120 mm² (Type 1023) | 120.0 mm² | 51.2 | 3890 | 7280 | 614 | Standard MGM 109 Type 1023 / 1024 configurations
| MGM 109 Type 1023 3C × 185 mm² 640/1100V DWA | 3 × 185 mm² (Type 1023) | 185.0 mm² | 59.8 | 5980 | 10250 | 718 | Standard MGM 109 Type 1023 / 1024 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA).

## Electrical & ampacity
MGM 109 Type 1023 / 1024 Double-Armoured LV Feeder Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-double-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
4 × 16 mm² (Type 1024) | 1.15 | 96 | 86 | 2.29 | 2.5 | 3500
3 × 25 mm² (Type 1023) | 0.727 | 127 | 114 | 3.58 | 1.6 | 3500
3 × 50 mm² (Type 1023) | 0.387 | 190 | 171 | 7.15 | 0.85 | 3500
3 × 95 mm² (Type 1023) | 0.193 | 285 | 256 | 13.59 | 0.44 | 3500
3 × 120 mm² (Type 1023) | 0.153 | 330 | 297 | 17.16 | 0.36 | 3500
3 × 185 mm² (Type 1023) | 0.0991 | 425 | 382 | 26.46 | 0.25 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA).

## Technical data
MGM 109 Type 1023 / 1024 Double-Armoured LV Feeder Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-double-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | MGM 109 / BS (Type 1023 (3C) & Type 1024 (4C))
Key data | Rated voltage | 640/1100 V AC (1.1 kV underground coal-face LV system)
Key data | Armour | Double Wire (2 counter-helical GSW layers ('2'))
Key data | Armour conductance | ≥ 75 % of Phase (Copper wires mixed in DWA if required)
Key data | Insulation | 90 °C EPR GP4 (BS 7655-1.2 elastomeric insulation)
Key data | Outer sheath | FR-PVC Type (Mine flame-retardant Black PVC)
Electrical | Rated voltage U0/U | 640/1100 V AC (1.1 kV mining LV standard)
Electrical | Routine AC dielectric test | 3,500 V AC for 5 minutes
Electrical | Min. armour conductance | ≥ 75 % of the conductance of the largest
Electrical | Max. conductor operating temp. | +90 °C continuous (EPR) · +250 °C
Thermal | Operating temperature range | -20 °C to +85 °C fixed roadway / shaft
Thermal | Minimum installation temp. | 0 °C
Mechanical | Min. bending radius | 12 × overall diameter (D) for Double Wire
Mechanical | Torque-balanced shaft capability | Counter-helical inner & outer DWA layers
Resistance | Mine flame retardancy | BS EN 60332-1-2 & NCB / British Coal
Resistance | Corrosion & mine water protection | Galvanized steel wires + bitumen/PVC
Standards | Primary specification | British Coal Specification MGM 109 & BS 6708
Standards | Type code breakdown | 1 = 640/1100 V · 0 = Unscreened · 2 = DWA ·
Identification | Core identification | Type 1023: Brown, Black, Grey (or Red
Identification | Outer sheath colour | Black (embossed with MGM 109 Type 1023

## Construction
MGM 109 Type 1023 / 1024 Double-Armoured LV Feeder Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-double-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 2 stranded copper conductors | BS EN 60228 Class 2 circular stranded annealed copper (16 mm² to 185 mm², 3-core or | MGM 109 / BS 6708
2 | Type GP4 EPR rubber insulation (90 °C) | Cross-linked ethylene-propylene elastomer Type GP4 per BS 7655-1.2 | BS 6708
3 | Extruded PVC inner bedding | Flame-retardant PVC bedding filling core interstices | MGM 109
4 | Double wire armour (DWA — 2 counter | Two counter-helical layers of galvanized steel wires (+ tinned Cu wires to meet ≥ 75 % | MGM 109 Digit 3 = '2'
5 | Heavy-duty mining FR-PVC outer sheath | Abrasion-, oil-, and mine-flame-retardant PVC outer sheath (RAL 9005 Black) | MGM 109 / BS 6708
| MGM 109 Type 1023 (640/1100 V, 3-Core Unscreened DWA) | 3-core (Brown, Black, Grey) 640/1100 V double-wire-armoured roadway power feeder (16 to 185 mm²).
| MGM 109 Type 1024 (640/1100 V, 4-Core Unscreened DWA) | 4-core (3 phases + pilot/neutral, 2.5 to 120 mm²) 640/1100 V double-wire-armoured mining feeder.

## Quality and supply
MGM 109 Type 1023 / 1024 Double-Armoured LV Feeder Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-double-armoured-lv-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 109 / BS 6708 (Type 1023 3-Core & Type 1024 4-Core 640/1100 V DWA). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric & insulation resistance — 3,500 V AC for 5 min per MGM 109 / BS 6708 | 100 % of drums
Routine test | Phase & DWA armour DC resistance ratio — Armour conductance ≥ 75 % of largest phase conductor | 100 % of drums
Sample test | GP4 EPR hot-set & galvanizing coat weight — BS 7655-1.2 EPR & BS EN 10257-1 armour wire checks | Per production batch
Type test | Underground mining flame & impact crush test — Pass MGM 109 / BS 6708 mechanical & flame approval | Type approval
Standard / approval | British Coal MGM 109
Standard / approval | BS 6708
Standard / approval | CE / UKCA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MGM 109 TYPE 1023 / 1024
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP