## Request a quote
Request a quotation for MGM 109 Type 3023
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for MGM 109 Type 3023.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mgm-109-type-3023-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MGM 109 Type 3023 Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-type-3023-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| MGM 109 Type 3023 3C × 25 mm² DWA | 3 × 25 mm² | 25.0 mm² | 34.6 | 720 | 2680 | 415 | Standard MGM 109 Type 3023 configurations
| MGM 109 Type 3023 3C × 50 mm² DWA | 3 × 50 mm² | 50.0 mm² | 41 | 1440 | 3950 | 492 | Standard MGM 109 Type 3023 configurations
| MGM 109 Type 3023 3C × 70 mm² DWA (Cu/GSW) | 3 × 70 mm² | 70.0 mm² | 45.4 | 2160 | 4980 | 545 | Standard MGM 109 Type 3023 configurations
| MGM 109 Type 3023 3C × 95 mm² DWA (Cu/GSW) | 3 × 95 mm² | 95.0 mm² | 50.2 | 2980 | 6280 | 602 | Standard MGM 109 Type 3023 configurations
| MGM 109 Type 3023 3C × 120 mm² DWA (Cu/GSW) | 3 × 120 mm² | 120.0 mm² | 54.6 | 3760 | 7490 | 655 | Standard MGM 109 Type 3023 configurations
| MGM 109 Type 3023 3C × 185 mm² DWA (Cu/GSW) | 3 × 185 mm² | 185.0 mm² | 63 | 5790 | 10420 | 756 | Standard MGM 109 Type 3023 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA).

## Electrical & ampacity
MGM 109 Type 3023 Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-type-3023-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3 × 25 mm² | 0.734 | 132 | 119 | 3.58 | 1.56 | 6500
3 × 50 mm² | 0.391 | 194 | 175 | 7.15 | 0.82 | 6500
3 × 70 mm² | 0.27 | 240 | 216 | 10.01 | 0.58 | 6500
3 × 95 mm² | 0.195 | 290 | 261 | 13.59 | 0.43 | 6500
3 × 120 mm² | 0.154 | 335 | 301 | 17.16 | 0.35 | 6500
3 × 185 mm² | 0.1 | 435 | 391 | 26.46 | 0.24 | 6500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA).

## Technical data
MGM 109 Type 3023 Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-type-3023-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Specification | MGM 109 Type (3.3 kV · Unscreened (0) · DWA (2) · 3C)
Key data | Rated voltage | 1.9/3.3 kV AC (6.5 kV AC / 5 min dielectric test)
Key data | Core screening | Unscreened (0) (Collective DWA metallic earth return)
Key data | Armouring | Double Wire (Counter-helical GSW/Cu (≥ 75 % earth))
Key data | Insulation | Type GP4 EPR (90 °C cross-linked rubber BS 7655)
Key data | Outer sheath | Mining FR-PVC (Heavy-duty flame-retardant Black PVC)
Electrical | Rated voltage U0/U | 1.9/3.3 kV AC (1900/3300 V)
Electrical | AC dielectric test voltage | 6,500 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Metallic armour conductance | ≥ 75 % of the conductance of one phase
Thermal | Operating temperature range | -15 °C to +90 °C (fixed installation)
Thermal | Minimum installation temp. | 0 °C
Mechanical | Min. bending radius | 12 × overall diameter (D) for DWA mining
Mechanical | Armour construction | Two counter-helical layers of round
Resistance | Flame retardance | BS EN 60332-1-2 & British Coal underground
Resistance | Water, oil & abrasion | Heavy mining PVC oversheath resists acidic
Standards | Primary specification | British Coal Specification MGM 109 (Type
Standards | Material standards | BS EN 60228 · BS 7655-1.2 (GP4 EPR) · BS EN
Identification | Core identification | 3-Core: Brown, Black, Grey
Identification | Outer sheath colour | Black embossed 'MGM 109 TYPE 3023 1900/3300V'

## Construction
MGM 109 Type 3023 Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-type-3023-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper conductor | BS EN 60228 Class 2 circular stranded tinned annealed copper (16 to 185 mm²) | MGM 109 / BS EN 60228
2 | Type GP4 EPR rubber insulation (90 °C) | Cross-linked ethylene-propylene elastomer Type GP4 per BS 7655-1.2 | MGM 109 / BS 7655-1.2
3 | Extruded PVC inner bedding | Flame-retardant extruded PVC inner bedding | MGM 109
4 | Double Wire Armour (DWA ≥ 75 % | Two counter-helical layers of galvanized steel wires (+ tinned Cu wires) with separator | MGM 109 / BS 6708
5 | Mining flame-retardant PVC outer sheath | Heavy-duty abrasion- and flame-retardant PVC outer sheath, Black | MGM 109 / BS 7655
| MGM 109 Type 3023 Branch Feeders (3C × 16, 25, 35, 50 mm²) | 1.9/3.3 kV unscreened DWA feeders for district pumps, haulages, and auxiliary substations.
| MGM 109 Type 3023 Trunk Feeders (3C × 70, 95, 120, 150, 185 mm²) | 1.9/3.3 kV unscreened DWA main shaft and roadway trunk cables with ≥ 75 % earth conductance.

## Quality and supply
MGM 109 Type 3023 Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-109-type-3023-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 109 / BS 6708 (Type 3023 1.9/3.3 kV Unscreened DWA). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 6.5 kV AC dielectric & insulation resistance — 6,500 V AC for 5 min per MGM 109 / BS 6708 | 100 % of drums
Routine test | Phase & DWA armour DC resistance ratio — DWA conductance ≥ 75 % of one phase conductor | 100 % of drums
Sample test | GP4 EPR hot-set & galvanizing coat weight — BS 7655-1.2 EPR & BS EN 10257-1 wire checks | Per production batch
Type test | Underground mining flame & impact test — Pass MGM 109 / BS 6708 mechanical and flame qualification | Type approval
Standard / approval | British Coal MGM 109 Type 3023
Standard / approval | BS 6708
Standard / approval | CE / UKCA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MGM 109 TYPE 3023 1900/3300V
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP