## Request a quote
Request a quotation for MGM 111 Type 21
Application engineer · MGM & BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mgm-111-type-21-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MGM 111 Type 21 Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-111-type-21-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 111 / BS 6708 Type 21. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| MGM 111 Type 21 4×2.5 | 4×2.5 | 14 | 17.7 | 19.2 | 96 | 610 | 115 | MGM 111 Type 21 — 4 Equal Cores (2.5–25 mm², 640/1,100 V)
| MGM 111 Type 21 4×4 | 4×4 | 12 | 19.3 | 21 | 154 | 760 | 126 | MGM 111 Type 21 — 4 Equal Cores (2.5–25 mm², 640/1,100 V)
| MGM 111 Type 21 4×6 | 4×6 | 10 | 21.2 | 23 | 230 | 940 | 138 | MGM 111 Type 21 — 4 Equal Cores (2.5–25 mm², 640/1,100 V)
| MGM 111 Type 21 4×10 | 4×10 | 8 | 24.7 | 26.8 | 384 | 1340 | 161 | MGM 111 Type 21 — 4 Equal Cores (2.5–25 mm², 640/1,100 V)
| MGM 111 Type 21 4×16 | 4×16 | 6 | 27.8 | 30.2 | 614 | 1790 | 181 | MGM 111 Type 21 — 4 Equal Cores (2.5–25 mm², 640/1,100 V)
| MGM 111 Type 21 4×25 | 4×25 | 4 | 32.2 | 35 | 960 | 2490 | 210 | MGM 111 Type 21 — 4 Equal Cores (2.5–25 mm², 640/1,100 V)
| MGM 111 Type 21 3×35+1×25 | 3×35+1×25 | 2 | 35.3 | 38.4 | 1248 | 3050 | 230 | MGM 111 Type 21 — 3 Phase + 1 Earth Core (35–150 mm², 640/1,100 V)
| MGM 111 Type 21 3×50+1×25 | 3×50+1×25 | 1 | 39.4 | 42.8 | 1680 | 3840 | 257 | MGM 111 Type 21 — 3 Phase + 1 Earth Core (35–150 mm², 640/1,100 V)
| MGM 111 Type 21 3×70+1×35 | 3×70+1×35 | 2/0 | 43.7 | 47.5 | 2352 | 4920 | 285 | MGM 111 Type 21 — 3 Phase + 1 Earth Core (35–150 mm², 640/1,100 V)
| MGM 111 Type 21 3×95+1×50 | 3×95+1×50 | 3/0 | 48.6 | 52.8 | 3216 | 6210 | 317 | MGM 111 Type 21 — 3 Phase + 1 Earth Core (35–150 mm², 640/1,100 V)
| MGM 111 Type 21 3×120+1×70 | 3×120+1×70 | 4/0 | 52.6 | 57.2 | 4128 | 7490 | 343 | MGM 111 Type 21 — 3 Phase + 1 Earth Core (35–150 mm², 640/1,100 V)
| MGM 111 Type 21 3×150+1×95 | 3×150+1×95 | 300 kcmil | 57 | 62 | 5232 | 9020 | 372 | MGM 111 Type 21 — 3 Phase + 1 Earth Core (35–150 mm², 640/1,100 V)
Dimensions and weights are typical values per MGM 111 / BS 6708 Type 21. Minimum fixed bending radius shown is 6 × OD.

## Electrical & current ratings
MGM 111 Type 21 Cable – Electrical & current ratings (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-111-type-21-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 111 / BS 6708 Type 21. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
2.5 | 14 | 8.21 | 30 | 25
4 | 12 | 5.09 | 41 | 34
6 | 10 | 3.39 | 53 | 44
10 | 8 | 1.95 | 74 | 61
16 | 6 | 1.24 | 99 | 82
25 | 4 | 0.795 | 131 | 108
35 | 2 | 0.565 | 162 | 135
50 | 1 | 0.393 | 202 | 168
70 | 2/0 | 0.277 | 250 | 207
95 | 3/0 | 0.21 | 301 | 250
120 | 4/0 | 0.164 | 352 | 292
150 | 300 kcmil | 0.132 | 404 | 335
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
MGM 111 Type 21 Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-111-type-21-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 111 / BS 6708 Type 21. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 640/1,100 V (660/1,100 V AC · 3.0 kV test)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −25…+80 °C (Flexing (−40…+80 °C fixed))
Key data | Bending radius | 6–8 × OD (6 × OD fixed · 8 × OD flexing)
Key data | Construction | 4C + PWA (3 phase + 1 earth · steel PWA armour)
Key data | Size range | 2.5–150 mm² (4-core (3P+E) · Class 5 SnCu)
Electrical | Rated voltage U0/U | 640/1,100 V (660/1,100 V AC · 1.1 kV mining system)
Electrical | AC test voltage | 3000 V AC (50 Hz, 5 min)
Electrical | Conductor stranding | IEC 60228 / BS EN 60228 Class 5 tinned copper
Electrical | Core configuration | 4 unscreened EPR cores (3 phase + 1 protective earth) around cradle
Electrical | Armour conductance | Galvanised steel PWA supplements the internal copper earth core
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −25 °C to +80 °C
Thermal | Temperature, fixed | −40 °C to +80 °C
Mechanical | Min. bending radius, fixed | 6 × overall diameter
Mechanical | Min. bending radius, moving | 8 × overall diameter
Mechanical | Armour type | Pliable wire armour (PWA) of stranded galvanised steel wires
Mechanical | Crush & impact protection | Central rubber cradle + inner bedding + steel PWA
Resistance | Flame retardance | IEC 60332-1-2 / BS EN 60332-1-2 self-extinguishing
Resistance | Oil & hydraulic fluids | EN 60811-404 mineral oil & hydraulic emulsion resistant (PCP)
Resistance | Mine water & humidity | Resistant to wet coal-mine roadways, sludge and grease
Resistance | Abrasion & tear | Heavy-duty RS4/EM2 polychloroprene outer jacket
Standards | Primary specification | TTK MGM 111 Type 21 / BS 6708 Type 21
Standards | Compound standards | BS 7655-1.2 GP8 (EPR) & BS 7655-2.1 RS4 / EN 50363 EM2 (PCP)
Standards | Conductor standard | IEC 60228 / BS EN 60228 Class 5
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | Colour-coded or numbered phase cores + earth core
Identification | Sheath marking | TEBAOFLEX MGM 111 TYPE 21 [Size] 640/1100V MINING CABLE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V / 1100 V)

## Construction
MGM 111 Type 21 Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-111-type-21-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 111 / BS 6708 Type 21. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned copper conductor | Fine-stranded annealed tinned copper wire (IEC 60228 / BS EN 60228 Class 5) | IEC 60228 Class 5
2 | EPR core insulation | Cross-linked ethylene-propylene rubber compound Type GP8 (+90 °C rated) | BS 7655-1.2 GP8 / MGM 111
3 | Elastomeric cradle center | Extruded rubber cradle separator keeping the 4 cores symmetrically spaced under crush load | MGM 111 / BS 6708 Type 21
4 | Elastomeric inner bedding | Extruded vulcanised rubber inner sheath consolidating the 4-core cradle assembly | MGM 111 inner bedding
5 | Pliable wire armour (PWA) | Stranded galvanised steel wire armour (PWA) providing high crush protection and fault-return conductance | MGM 111 / BS 6708 PWA
6 | Heavy-duty PCP outer sheath | Cross-linked polychloroprene (PCP / Type RS4 / EM2) extra-heavy-duty outer sheath, black | BS 7655-2.1 / IEC 60332-1-2
| MGM 111 Type 21 Equal Cores (4×2.5 to 4×25) | 4 equal-cross-section EPR cores (3 phase + 1 earth) with central cradle, inner bedding, PWA and PCP sheath
| MGM 111 Type 21 Reduced Earth (3×35+25 to 3×150+95) | 3 full-size EPR phase cores + 1 earth core + central cradle, inner bedding, PWA and PCP sheath

## Quality and supply
MGM 111 Type 21 Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-111-type-21-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 111 / BS 6708 Type 21. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 3.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (tinned copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — MGM 111 / BS 6708 Type 21 | Type approval
Standard / approval | MGM 111 / BS 6708 Type 21
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MGM 111 TYPE 21 [Size] 640/1100 V MINING CABLE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request