## Request a quote
Request a quotation for MGM 112 Type 331
Application engineer · MGM & BS 6708 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mgm-112-type-331-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MGM 112 Type 331 Cable – Dimensions & weights (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-112-type-331-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 112 / BS 6708 Type 331. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| MGM 112 Type 331 3×16+1×16 | 3×16+1×16 | 6 | 35 | 38 | 730 | 2450 | 228 | MGM 112 Type 331 — 3 Screened Phase + Equal Earth Core (16–25 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×25+1×25 | 3×25+1×25 | 4 | 38.8 | 42.2 | 1086 | 3120 | 253 | MGM 112 Type 331 — 3 Screened Phase + Equal Earth Core (16–25 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×25+1×16 | 3×25+1×16 | 4 | 38.5 | 41.8 | 1000 | 3040 | 251 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×35+1×25 | 3×35+1×25 | 2 | 41.8 | 45.4 | 1380 | 3720 | 272 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×50+1×25 | 3×50+1×25 | 1 | 46 | 50 | 1830 | 4590 | 300 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×70+1×35 | 3×70+1×35 | 2/0 | 50.4 | 54.8 | 2520 | 5740 | 329 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×95+1×50 | 3×95+1×50 | 3/0 | 55.4 | 60.2 | 3420 | 7120 | 361 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×120+1×70 | 3×120+1×70 | 4/0 | 59.6 | 64.8 | 4360 | 8490 | 389 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
| MGM 112 Type 331 3×150+1×95 | 3×150+1×95 | 300 kcmil | 63.9 | 69.5 | 5490 | 10120 | 417 | MGM 112 Type 331 — 3 Screened Phase + Reduced Earth Core (25–150 mm², 1.9/3.3 kV)
Dimensions and weights are typical values per MGM 112 / BS 6708 Type 331. Minimum fixed bending radius shown is 6 × OD.

## Electrical & current ratings
MGM 112 Type 331 Cable – Electrical & current ratings (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-112-type-331-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 112 / BS 6708 Type 331. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
16 | 6 | 1.24 | 99 | 82
25 | 4 | 0.795 | 131 | 108
35 | 2 | 0.565 | 162 | 135
50 | 1 | 0.393 | 202 | 168
70 | 2/0 | 0.277 | 250 | 207
95 | 3/0 | 0.21 | 301 | 250
120 | 4/0 | 0.164 | 352 | 292
150 | 300 kcmil | 0.132 | 404 | 335
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
MGM 112 Type 331 Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-112-type-331-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 112 / BS 6708 Type 331. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.9/3.3 kV (1,900/3,300 V AC · 7.5 kV test)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −25…+80 °C (Flexing (−40…+80 °C fixed))
Key data | Bending radius | 6–8 × OD (6 × OD fixed · 8 × OD flexing)
Key data | Construction | 3S+1E + PWA (3 screened phase + 1 earth + steel PWA)
Key data | Size range | 16–150 mm² (4-core cradle lay · Class 5 SnCu)
Electrical | Rated voltage U0/U | 1.9/3.3 kV (1,900/3,300 V AC · Um 3.6 kV)
Electrical | AC test voltage | 7.5 kV AC (50 Hz, 5 min)
Electrical | Conductor stranding | IEC 60228 / BS EN 60228 Class 5 tinned copper
Electrical | Phase core screening | Individual tinned-copper/nylon braid over each of the 3 phase cores
Electrical | Protective earth path | 1 dedicated unscreened copper earth core + 3 phase screens + steel PWA
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −25 °C to +80 °C
Thermal | Temperature, fixed | −40 °C to +80 °C
Mechanical | Min. bending radius, fixed | 6 × overall diameter
Mechanical | Min. bending radius, moving | 8 × overall diameter
Mechanical | Armour construction | Galvanised steel pliable wire armour (PWA) in multi-wire strands
Mechanical | Impact & crush duty | Extra-heavy underground roadway & rock-fall duty
Resistance | Flame retardance | IEC 60332-1-2 / BS EN 60332-1-2 underground mine flame test
Resistance | Oil & hydraulic emulsion | EN 60811-404 mineral oil, grease & hydraulic fluid resistant
Resistance | Water & mine dampness | Resistant to wet coal-mine roadways, sludge and grease
Resistance | Abrasion & tear | Heavy-duty RS4/EM2 polychloroprene outer sheath
Standards | Primary specification | TTK MGM 112 Type 331 / BS 6708 Type 331
Standards | Compound standards | BS 7655-1.2 GP8 (EPR) & BS 7655-2.1 RS4 / EN 50363 EM2 (PCP)
Standards | Conductor standard | IEC 60228 / BS EN 60228 Class 5
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | 3 screened phase cores + 1 unscreened earth core in cradle lay
Identification | Sheath marking | TEBAOFLEX MGM 112 TYPE 331 [Size] 1900/3300V MINING CABLE
Identification | Customs tariff (HS) | 8544.60 (insulated electric conductors > 1000 V)

## Construction
MGM 112 Type 331 Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-112-type-331-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 112 / BS 6708 Type 331. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned copper conductor | Fine-stranded annealed tinned copper wire (IEC 60228 / BS EN 60228 Class 5) | IEC 60228 Class 5
2 | MV EPR core insulation | Cross-linked ethylene-propylene rubber compound Type GP8 (+90 °C rated for 1.9/3.3 kV) | BS 7655-1.2 GP8 / MGM 112
3 | Individual phase screen | Composite tinned-copper and nylon (polyamide) braided earth screen over each of the 3 phase cores | MGM 112 / BS 6708 Type 331
4 | Elastomeric cradle center | Extruded rubber cradle separator keeping the 3 screened phase cores and 1 earth core symmetrically spaced | MGM 112 / BS 6708
5 | Elastomeric inner bedding | Extruded vulcanised rubber inner sheath over the 4-core cradle assembly | MGM 112 inner bedding
6 | Pliable wire armour (PWA) | Stranded galvanised steel wire armour (PWA) providing high crush protection and fault-return conductance | MGM 112 / BS 6708 PWA
7 | Heavy-duty PCP outer sheath | Cross-linked polychloroprene (PCP / Type RS4 / EM2) extra-heavy-duty outer sheath, black | BS 7655-2.1 / IEC 60332-1-2
| MGM 112 Type 331 Equal Earth (3×16+16 to 3×25+25) | 3 individually screened 1.9/3.3 kV phase cores + 1 equal-size earth core around cradle + PWA + PCP sheath
| MGM 112 Type 331 Reduced Earth (3×35+25 to 3×150+95) | 3 individually screened 1.9/3.3 kV phase cores + 1 earth core around cradle + PWA + PCP sheath

## Quality and supply
MGM 112 Type 331 Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-112-type-331-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on MGM 112 / BS 6708 Type 331. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 7.5 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (tinned copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — MGM 112 / BS 6708 Type 331 | Type approval
Standard / approval | MGM 112 / BS 6708 Type 331
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MGM 112 TYPE 331 [Size] 1900/3300 V MINING CABLE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request