## Request a quote
Request a quotation for MGM 118 Type 6110
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for MGM 118 Type 6110.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mgm-118-type-6110-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
MGM 118 Type 6110 Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-118-type-6110-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| MGM 118 Type 6110 3C × 35 mm² Cu-Scr SWA | 3 × 35 mm² | 35.0 mm² | 42.4 | 1240 | 3420 | 424 | Standard MGM 118 Type 6110 configurations
| MGM 118 Type 6110 3C × 50 mm² Cu-Scr SWA | 3 × 50 mm² | 50.0 mm² | 45.8 | 1690 | 4080 | 458 | Standard MGM 118 Type 6110 configurations
| MGM 118 Type 6110 3C × 70 mm² Cu-Scr SWA | 3 × 70 mm² | 70.0 mm² | 49.6 | 2360 | 4940 | 496 | Standard MGM 118 Type 6110 configurations
| MGM 118 Type 6110 3C × 95 mm² Cu-Scr SWA | 3 × 95 mm² | 95.0 mm² | 54.2 | 3180 | 6020 | 542 | Standard MGM 118 Type 6110 configurations
| MGM 118 Type 6110 3C × 120 mm² Cu-Scr SWA | 3 × 120 mm² | 120.0 mm² | 58 | 3980 | 7120 | 580 | Standard MGM 118 Type 6110 configurations
| MGM 118 Type 6110 3C × 185 mm² Cu-Scr SWA | 3 × 185 mm² | 185.0 mm² | 66.4 | 6080 | 9680 | 664 | Standard MGM 118 Type 6110 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA).

## Electrical & ampacity
MGM 118 Type 6110 Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-118-type-6110-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3 × 35 mm² | 0.529 | 156 | 140 | 5.01 | 1.12 | 11000
3 × 50 mm² | 0.391 | 192 | 173 | 7.15 | 0.82 | 11000
3 × 70 mm² | 0.27 | 240 | 216 | 10.01 | 0.58 | 11000
3 × 95 mm² | 0.195 | 288 | 259 | 13.59 | 0.43 | 11000
3 × 120 mm² | 0.154 | 335 | 301 | 17.16 | 0.35 | 11000
3 × 185 mm² | 0.1 | 432 | 389 | 26.46 | 0.24 | 11000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA).

## Technical data
MGM 118 Type 6110 Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-118-type-6110-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Specification | MGM 118 Type (6.6 kV · Screened (1) · SWA (1) · 3C)
Key data | Rated voltage | 3.8/6.6 kV AC (11 kV AC / 5 min dielectric test)
Key data | Phase screens | Semi-Con + Cu (Radial-field screened per core)
Key data | Armouring | Single Wire (Galvanized steel + Cu wires (≥ 75 %))
Key data | HV insulation | Type GP5 HV-EPR (90 °C PD-free rubber BS 7655-1.2)
Key data | Partial discharge | ≤ 5 pC @ 1.73 U0 (100 % routine PD verified)
Electrical | Rated voltage U0/U | 3.8/6.6 kV AC (3800/6600 V)
Electrical | AC dielectric test voltage | 11,000 V AC for 5 minutes
Electrical | Partial discharge (PD) limit | ≤ 5 pC at 1.73 × U0 (6.6 kV)
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Combined screen + armour conductance | ≥ 75 % of the conductance of one phase
Thermal | Operating temperature range | -15 °C to +90 °C (fixed installation)
Thermal | Minimum installation temp. | 0 °C
Mechanical | Min. bending radius | 10 × overall diameter (D) for screened 6.6
Mechanical | Armour construction | Single layer of galvanized steel + tinned
Resistance | Flame retardance | BS EN 60332-1-2 & British Coal MGM 118
Resistance | Fault safety | Individual Cu core screens confine
Standards | Primary specification | British Coal Specification MGM 118 (Type
Standards | Material standards | BS EN 60228 · BS 7655-1.2 (GP5 EPR) · BS EN
Identification | Core identification | 3-Core: Brown, Black, Grey (or numbered 1
Identification | Outer sheath colour | Black (or Red HV) embossed 'MGM 118 TYPE

## Construction
MGM 118 Type 6110 Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-118-type-6110-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper conductor | BS EN 60228 Class 2 circular compacted tinned annealed copper (25 to 185 mm²) | MGM 118 / BS EN 60228
2 | Triple-extruded Semi-Con + GP5 HV-EPR | Bonded semi-con conductor screen + 90 °C Type GP5 HV-EPR (BS 7655-1.2) + strippable | MGM 118 / BS 7655-1.2
3 | Individual tinned copper tape phase | Helically lapped tinned annealed copper tape over each core | MGM 118 Type 6110
4 | Extruded PVC inner bedding | Flame-retardant extruded PVC inner bedding | MGM 118
5 | Single Wire Armour (SWA ≥ 75 % | Single helical layer of galvanized steel wires + tinned copper wires (combined | MGM 118 / BS 6708
6 | Mining flame-retardant PVC outer sheath | Heavy-duty abrasion- and flame-retardant PVC outer sheath, Black or HV Red | MGM 118 / BS 7655
| MGM 118 Type 6110 District Feeders (3C × 25, 35, 50, 70 mm²) | 3.8/6.6 kV individually copper-screened SWA feeders for 6.6 kV/1.1 kV flameproof district transformers.
| MGM 118 Type 6110 Main Trunk Feeders (3C × 95, 120, 150, 185 mm²) | High-ampacity 6.6 kV radial-field screened SWA trunk cables for main underground intake roadways.

## Quality and supply
MGM 118 Type 6110 Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mgm-118-type-6110-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on British Coal MGM 118 / BS 6708 (Type 6110 3.8/6.6 kV Screened SWA). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Partial discharge (PD ≤ 5 pC) & 11 kV AC test — PD ≤ 5 pC @ 1.73 U0; 11,000 V AC for 5 min per MGM 118 | 100 % of drums
Routine test | Phase, Cu screen & SWA DC resistance — Combined screen + armour conductance ≥ 75 % of one phase | 100 % of drums
Sample test | GP5 HV-EPR hot-set & strippable semi-con peel — BS 7655-1.2 & MGM 118 core screen peel force | Per production batch
Type test | Mining impact crush, impulse & flame test — Pass MGM 118 / BS 6708 60 kV BIL and flame approval | Type approval
Standard / approval | British Coal MGM 118 Type 6110
Standard / approval | BS 6708
Standard / approval | CE / UKCA
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX MGM 118 TYPE 6110 3800/6600V
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP