## Request a quote
Request a quotation for Mineral-Insulated Heating Cable
Application engineer · industrial heat-tracing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mineral-insulated-heating-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Mineral-Insulated Heating Cable – Resistance steps, sheath alloy, OD & mass (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1, IEC 60800 & IEEE 515. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | MI cable designation | Rated Vac | Cores count | Res. @20°C Ω/m | Conductor alloy | Sheath alloy | Max exp. °C | Cable OD mm | Mass ≈ kg/km
| MIQ-1C-825-0.003 · 600 V | 600 Vac | 1C | 0.003 | Copper | Alloy 825 | 800 | 6.4 | 155
| MIQ-1C-825-0.006 · 600 V | 600 Vac | 1C | 0.006 | Copper | Alloy 825 | 800 | 5.5 | 112
| MIQ-1C-825-0.015 · 600 V | 600 Vac | 1C | 0.015 | Copper | Alloy 825 | 800 | 4.8 | 82
| MIQ-1C-825-0.040 · 600 V | 600 Vac | 1C | 0.04 | CuNi Alloy | Alloy 825 | 800 | 4.6 | 76
| MIQ-1C-825-0.100 · 600 V | 600 Vac | 1C | 0.1 | CuNi Alloy | Alloy 825 | 800 | 4.3 | 66
| MIQ-1C-825-0.250 · 600 V | 600 Vac | 1C | 0.25 | CuNi44 | Alloy 825 | 800 | 4.3 | 65
| MIQ-1C-825-0.650 · 600 V | 600 Vac | 1C | 0.65 | CuNi44 | Alloy 825 | 800 | 4 | 56
| MIQ-1C-825-1.600 · 600 V | 600 Vac | 1C | 1.6 | NiCr 80/20 | Alloy 825 | 800 | 3.7 | 48
| MIQ-1C-825-4.000 · 500 V | 500 Vac | 1C | 4 | NiCr 80/20 | Alloy 825 | 800 | 3.2 | 36
| MIQ-2C-825-0.030 · 600 V | 600 Vac | 2C | 0.03 | Copper | Alloy 825 | 800 | 8.2 | 225
| MIQ-2C-825-0.080 · 600 V | 600 Vac | 2C | 0.08 | CuNi Alloy | Alloy 825 | 800 | 7.3 | 178
| MIQ-2C-825-0.200 · 600 V | 600 Vac | 2C | 0.2 | CuNi Alloy | Alloy 825 | 800 | 6.4 | 138
| MIQ-2C-825-0.500 · 600 V | 600 Vac | 2C | 0.5 | CuNi44 | Alloy 825 | 800 | 5.8 | 112
| MIQ-2C-316L-1.250 · 500 V | 500 Vac | 2C | 1.25 | CuNi44 | SS 316L | 650 | 5.2 | 90
| MIQ-2C-825-3.600 · 500 V | 500 Vac | 2C | 3.6 | NiCr 80/20 | Alloy 825 | 800 | 4.9 | 80
| MIQ-2C-825-11.500 · 500 V | 500 Vac | 2C | 11.5 | NiCr 80/20 | Alloy 825 | 800 | 4 | 54
All sizes are available in Alloy 825 (UNS N08825), Inconel 600 (UNS N06600), SS 316L (UNS S31603) or CuNi 70/30 sheath; 2C resistance is loop resistance per metre.

## Sheath alloy temperature, watt
Mineral-Insulated Heating Cable – Sheath alloy temperature, watt density & corrosion selection (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1, IEC 60800 & IEEE 515. Values for your order are confirmed in the quotation.
Sheath alloy · UNS | Max maintain °C | Max exposure °C | Max output W/m | Chloride SCC immunity | Primary industrial environment
Alloy 825 (UNS N08825) | 600 | 800 | 270 | Immune (42% Ni) | Refineries, chlorides, sour gas, acids & superheated steam
Inconel 600 (UNS N06600) | 600 | 800 | 270 | Immune (72% Ni) | Extreme oxidation, nuclear, molten salt & furnace piping
Stainless Steel 316L (UNS S31603) | 500 | 650 | 200 | Moderate (avoid Cl⁻) | General high-temperature steam, chemical & process vessels
Cupro-Nickel 70/30 (UNS C71500) | 300 | 400 | 150 | High | Seawater, marine decks & medium-temperature process lines
Alloy 825 / 316L + FEP Jacket | 150 | 205 | 100 | Immune | Buried culverts, caustic washdown & wet chemical trenches
Alloy 825 (UNS N08825) is recommended over SS 304/316L wherever thermal insulation may become wet and leach trace chlorides onto the hot sheath.

## Technical data
Mineral-Insulated Heating Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1, IEC 60800 & IEEE 515. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Maintain temp. | Up to +600 °C (Max exposure +650 °C to +800 °C)
Key data | Linear output | Up to 270 W/m (200–270 W/m continuous thermal output)
Key data | Rated voltage | 300/500 & 600 V (1-core & 2-core 300/500 V or 600 Vac)
Key data | Dielectric | Compacted MgO (100 % inorganic non-ageing dielectric)
Key data | Outer sheath | Alloy 825 / 316L (Also Inconel 600 & Cupro-Nickel 70/30)
Key data | Min. bend radius | 6 × OD (Annealed metal tube (3.2–9.5 mm OD))
Electrical | Rated voltage | 300/500 Vac & 600 Vac (1-core and 2-core)
Electrical | Resistance range | 0.0028 to 28.0 Ω/m at +20 °C (±10 % tol.)
Electrical | Dielectric withstand | 2.0 to 2.5 kV AC RMS for 1 min (core-sheath)
Electrical | Insulation resistance | ≥ 1,000 MΩ at 1,000 Vdc (sealed factory unit)
Thermal | Max. maintain temp. | Up to +600 °C (Alloy 825 / Inconel 600)
Thermal | Max. sheath exposure | +650 °C (SS 316L) · +800 °C (Alloy 825 / 600)
Thermal | Linear watt density | Up to 200–270 W/m (depending on pipe T)
Thermal | Min. installation T | −60 °C (down to −196 °C cryogenic service)
Mechanical | Cable outer diameter | 3.2 mm to 9.5 mm seamless annealed metal tube
Mechanical | Min. bending radius | 6 × cable OD (hand-formable annealed sheath)
Mechanical | Impact & crush resistance | Exceeds 7 J impact & 2,000 N crush load
Mechanical | Hot-to-cold junction | Factory-brazed / laser-welded cold transition
Resistance | Fire & flammability | 100 % non-combustible inorganic metal + MgO
Resistance | Stress-corrosion cracking | Alloy 825 (42% Ni) immune to chloride SCC
Resistance | Chemical & oil resistance | Seamless alloy tube resists acids, H2S & oils
Resistance | Radiation resistance | Inorganic MgO + alloy withstands > 10⁷ Gy
Standards | Applicable standards | IEC 60079-30-1, IEC 60800, IEEE 515, ASTM E235
Standards | Sheath alloy standards | ASTM B423 (825), B167 (600) & A269 (316L)
Standards | Pressure test | Pneumatic / He-leak & hydrostatic sheath test
Standards | RoHS & REACH | Asbestos-free, RoHS & REACH compliant
Identification | Tag & laser marking | SS tag + laser print: Model, Ω/m, V, W, S/N
Identification | Sheath finish | Bright annealed metal (or orange FEP jacket)
Identification | Factory unit code | [1C/2C]-[Alloy]-[Ω/m]-[Heated L]-[Cold L]
Identification | Customs tariff (HS) | 8544.49 / 8516.80 (mineral-insulated heaters)

## Construction
Mineral-Insulated Heating Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1, IEC 60800 & IEEE 515. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid resistance heating conductor(s) | 1 or 2 solid conductors in oxygen-free copper, CuNi resistance alloys or NiCr 80/20 (0.0028 to 28.0 Ω/m at 20 °C) | IEC 60079-30-1 / IEEE 515
2 | Compacted high-purity magnesium oxide (MgO) | High-density compressed inorganic MgO mineral dielectric powder providing high thermal conductivity and non-melting electrical isolation | IEC 60800 / ASTM E235
3 | Seamless drawn metallic earth & barrier tube | Seamless TIG/laser-welded and drawn Alloy 825 (UNS N08825), Inconel 600 (UNS N06600), SS 316L or CuNi 70/30 continuous metal sheath | IEC 60079-30-1 / IEEE 515
4 | Annealed bright metal surface (or optional polymer jacket) | Bright-annealed bare alloy sheath for +600/+800 °C service (optional extruded FEP/HDPE oversheath for ≤ +200 °C corrosive/buried zones) | IEC 60079-30-1
| MI-825 / MI-600 · Seamless Alloy 825 or Inconel 600 Sheath | 300/500 V & 600 V · Maintain +600 °C · Max exposure +800 °C · 1C or 2C resistance core + compacted MgO + chloride-SCC-immune Alloy 825 / 600 sheath
| MI-316L · Seamless Stainless Steel 316L Sheath | 300/500 V & 600 V · Maintain +500 °C · Max exposure +650 °C · 1C or 2C resistance core + compacted MgO + annealed SS 316L sheath
| MI-CuNi · Cupro-Nickel 70/30 Sheath | 300/500 V · Maintain +300 °C · Max exposure +400 °C · High-ductility 70/30 cupro-nickel sheath for medium-temperature marine & industrial tracing

## Quality and supply
Mineral-Insulated Heating Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mineral-insulated-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1, IEC 60800 & IEEE 515. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage withstand test — 2.0 kV to 2.5 kV RMS AC for 1 min between resistance conductors and metal sheath | Every heating unit
Routine test | 1,000 Vdc MgO insulation resistance test — Insulation resistance ≥ 1,000 MΩ verified at 1,000 Vdc after hermetic end-seal brazing | Every heating unit
Routine test | Circuit DC resistance & cold-lead weld check — Total loop resistance verified within ±10 % at 20 °C and X-ray/visual inspection of hot-cold splice | Every heating unit
Sample test | Hydrostatic / helium sheath integrity & mandrel bend — Seamless tube pressure leak check and 6 × OD mandrel bend test followed by dielectric withstand | Production lot
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · [MIQ TAG] · [ALLOY 825 / 316L] · [V / W / Ω] · [HEATED L / COLD L] · IEC 60079-30-1 · SERIAL NO.
Supply | Delivery form: Factory-terminated heating units (cold leads + brass/SS glands) or bulk coils
Supply | Lengths: Custom engineered heated lengths with 1.5–3.0 m cold leads
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None