## Request a quote
Request a quotation for (N)3GHSSYCY
Application engineer · VDE mining & tunnel MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-3ghssycy-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)3GHSSYCY 3.6/6–18/30 kV Armoured MV Mining & Tunnel Cable – Dimensions & electrical data (3.6/6–18/30 kV) (48)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-3ghssycy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Construction (Phase + Earth + Control + ÜL) | U0/U | Cond. Ø max | Outer Ø min | Outer Ø max | Weight ≈ | Max tensile | R20 max | Capacitance | Inductance | Ampacity 30 °C | Isc (1 s) | Min. bend R | Series
| 3×25 + 3×16/3E + 3×2.5ST + ÜL | 3.6/6 | 6.4 | 42.7 | 45.7 | 3180 | 1125 | 0.78 | 0.36 | 0.32 | 131 | 3.58 | 457 | 3.6/6 kV (Um 7.2 kV)
| 3×25 + 3×25/3E + 3×2.5ST + ÜL | 3.6/6 | 6.1 | 47.2 | 52.1 | 4160 | 1125 | 0.78 |  |  | 139 | 3.58 | 521 | 3.6/6 kV (Um 7.2 kV)
| 3×35 + 3×16/3E + 3×2.5ST + ÜL | 3.6/6 | 7.6 | 45.3 | 48.3 | 3700 | 1575 | 0.554 | 0.41 | 0.3 | 162 | 5.01 | 483 | 3.6/6 kV (Um 7.2 kV)
| 3×35 + 3×25/3E + 3×2.5ST + ÜL | 3.6/6 | 7.2 | 49 | 54 | 4610 | 1575 | 0.554 |  |  | 172 | 5.01 | 540 | 3.6/6 kV (Um 7.2 kV)
| 3×50 + 3×25/3E + 3×2.5ST + ÜL | 3.6/6 | 9.1 | 49.5 | 53.5 | 4730 | 2250 | 0.386 | 0.47 | 0.29 | 202 | 7.15 | 535 | 3.6/6 kV (Um 7.2 kV)
| 3×70 + 3×35/3E + 3×2.5ST + ÜL | 3.6/6 | 10.8 | 53.2 | 57.2 | 5720 | 3150 | 0.272 | 0.53 | 0.28 | 250 | 10.01 | 572 | 3.6/6 kV (Um 7.2 kV)
| 3×95 + 3×50/3E + 3×2.5ST + ÜL | 3.6/6 | 12.7 | 58.2 | 62.2 | 7010 | 4275 | 0.206 | 0.61 | 0.27 | 301 | 13.59 | 622 | 3.6/6 kV (Um 7.2 kV)
| 3×120 + 3×70/3E + 3×2.5ST + ÜL | 3.6/6 | 14.3 | 62.7 | 66.7 | 8311 | 5400 | 0.161 | 0.67 | 0.26 | 352 | 17.16 | 667 | 3.6/6 kV (Um 7.2 kV)
| 3×150 + 3×70/3E + 3×2.5ST + ÜL | 3.6/6 | 16 | 67.6 | 71.6 | 9634 | 6750 | 0.129 | 0.74 | 0.25 | 404 | 21.45 | 716 | 3.6/6 kV (Um 7.2 kV)
| 3×185 + 3×120/3E + 3×2.5ST + ÜL | 3.6/6 | 17.7 | 71.7 | 75.7 | 11202 | 8325 | 0.106 | 0.8 | 0.25 | 461 | 26.46 | 757 | 3.6/6 kV (Um 7.2 kV)
| 3×25 + 3×16/3E + 3×2.5ST + ÜL | 6/10 | 6.4 | 45.7 | 48.7 | 3580 | 1125 | 0.78 | 0.32 | 0.33 | 131 | 3.58 | 487 | 6/10 kV (Um 12 kV)
| 3×25 + 3×25/3E + 3×2.5ST + ÜL | 6/10 | 6.1 | 47.2 | 52.7 | 4200 | 1125 | 0.78 |  |  | 139 | 3.58 | 527 | 6/10 kV (Um 12 kV)
| 3×35 + 3×16/3E + 3×2.5ST + ÜL | 6/10 | 7.6 | 47.8 | 50.8 | 4130 | 1575 | 0.554 | 0.36 | 0.31 | 162 | 5.01 | 508 | 6/10 kV (Um 12 kV)
| 3×35 + 3×25/3E + 3×2.5ST + ÜL | 6/10 | 7.2 | 49 | 54.6 | 4650 | 1575 | 0.554 |  |  | 172 | 5.01 | 546 | 6/10 kV (Um 12 kV)
| 3×50 + 3×25/3E + 3×2.5ST + ÜL | 6/10 | 9.1 | 50.8 | 54.8 | 4890 | 2250 | 0.386 | 0.42 | 0.3 | 202 | 7.15 | 548 | 6/10 kV (Um 12 kV)
| 3×70 + 3×35/3E + 3×2.5ST + ÜL | 6/10 | 10.8 | 55.1 | 59.1 | 5680 | 3150 | 0.272 | 0.47 | 0.28 | 250 | 10.01 | 591 | 6/10 kV (Um 12 kV)
| 3×95 + 3×50/3E + 3×2.5ST + ÜL | 6/10 | 12.7 | 60 | 64 | 7130 | 4275 | 0.206 | 0.54 | 0.27 | 301 | 13.59 | 640 | 6/10 kV (Um 12 kV)
| 3×120 + 3×70/3E + 3×2.5ST + ÜL | 6/10 | 14.3 | 63.9 | 67.9 | 8450 | 5400 | 0.161 | 0.59 | 0.26 | 352 | 17.16 | 679 | 6/10 kV (Um 12 kV)
| 3×150 + 3×70/3E + 3×2.5ST + ÜL | 6/10 | 16 | 68.9 | 72.9 | 9840 | 6750 | 0.129 | 0.66 | 0.25 | 404 | 21.45 | 729 | 6/10 kV (Um 12 kV)
| 3×185 + 3×120/3E + 3×2.5ST + ÜL | 6/10 | 17.7 | 73 | 77 | 11408 | 8325 | 0.106 | 0.74 | 0.25 | 461 | 26.46 | 770 | 6/10 kV (Um 12 kV)
| 3×25 + 3×16/3E + 3×2.5ST + ÜL | 8.7/15 | 6.4 | 49.1 | 53.1 | 3985 | 1125 | 0.78 | 0.22 | 0.36 | 139 | 3.58 | 531 | 8.7/15 kV (Um 18 kV)
| 3×35 + 3×16/3E + 3×2.5ST + ÜL | 8.7/15 | 7.6 | 50.4 | 54.4 | 4481 | 1575 | 0.554 | 0.29 | 0.33 | 172 | 5.01 | 544 | 8.7/15 kV (Um 18 kV)
| 3×50 + 3×25/3E + 3×2.5ST + ÜL | 8.7/15 | 9.1 | 53.9 | 57.9 | 5300 | 2250 | 0.386 | 0.33 | 0.31 | 215 | 7.15 | 579 | 8.7/15 kV (Um 18 kV)
| 3×70 + 3×35/3E + 3×2.5ST + ÜL | 8.7/15 | 10.8 | 57.6 | 61.6 | 6380 | 3150 | 0.272 | 0.38 | 0.3 | 265 | 10.01 | 616 | 8.7/15 kV (Um 18 kV)
| 3×95 + 3×50/3E + 3×2.5ST + ÜL | 8.7/15 | 12.7 | 63.1 | 67.1 | 7652 | 4275 | 0.206 | 0.43 | 0.29 | 319 | 13.59 | 671 | 8.7/15 kV (Um 18 kV)
| 3×120 + 3×70/3E + 3×2.5ST + ÜL | 8.7/15 | 14.3 | 67.4 | 71.4 | 8940 | 5400 | 0.161 | 0.47 | 0.28 | 371 | 17.16 | 714 | 8.7/15 kV (Um 18 kV)
| 3×150 + 3×70/3E + 3×2.5ST + ÜL | 8.7/15 | 16 | 72 | 76 | 10400 | 6750 | 0.129 | 0.54 | 0.27 | 428 | 21.45 | 760 | 8.7/15 kV (Um 18 kV)
| 3×185 + 3×120/3E + 3×2.5ST + ÜL | 8.7/15 | 17.7 | 75.6 | 79.6 | 11865 | 8325 | 0.106 | 0.58 | 0.26 | 488 | 26.46 | 796 | 8.7/15 kV (Um 18 kV)
| 3×25 + 3×16/3E + 3×2.5ST + ÜL | 12/20 | 6.4 | 52.6 | 56.6 | 3900 | 1125 | 0.78 | 0.2 | 0.37 | 139 | 3.58 | 566 | 12/20 kV (Um 24 kV)
| 3×35 + 3×16/3E + 3×2.5ST + ÜL | 12/20 | 7.6 | 53.6 | 57.6 | 5090 | 1575 | 0.554 | 0.25 | 0.35 | 172 | 5.01 | 576 | 12/20 kV (Um 24 kV)
| 3×50 + 3×25/3E + 3×2.5ST + ÜL | 12/20 | 9.1 | 56.8 | 60.8 | 5730 | 2250 | 0.386 | 0.28 | 0.33 | 215 | 7.15 | 608 | 12/20 kV (Um 24 kV)
| 3×70 + 3×35/3E + 3×2.5ST + ÜL | 12/20 | 10.8 | 61 | 65 | 6840 | 3150 | 0.272 | 0.32 | 0.31 | 265 | 10.01 | 650 | 12/20 kV (Um 24 kV)
| 3×95 + 3×50/3E + 3×2.5ST + ÜL | 12/20 | 12.7 | 66 | 70 | 8080 | 4275 | 0.206 | 0.36 | 0.3 | 319 | 13.59 | 700 | 12/20 kV (Um 24 kV)
| 3×120 + 3×70/3E + 3×2.5ST + ÜL | 12/20 | 14.3 | 69.9 | 73.9 | 9650 | 5400 | 0.161 | 0.39 | 0.29 | 371 | 17.16 | 739 | 12/20 kV (Um 24 kV)
| 3×150 + 3×70/3E + 3×2.5ST + ÜL | 12/20 | 16 | 71 | 75 | 10932 | 6750 | 0.129 | 0.43 | 0.28 | 428 | 21.45 | 750 | 12/20 kV (Um 24 kV)
| 3×185 + 3×120/3E + 3×2.5ST + ÜL | 12/20 | 17.7 | 78.7 | 82.7 | 12417 | 8325 | 0.106 | 0.47 | 0.27 | 488 | 26.46 | 827 | 12/20 kV (Um 24 kV)
| 3×35 + 3×16/3E + 3×2.5ST + ÜL | 14/25 | 7.6 | 57.6 | 61.6 | 5502 | 1575 | 0.554 | 0.21 | 0.37 | 172 | 5.01 | 616 | 14/25 kV (Um 30 kV)
| 3×50 + 3×25/3E + 3×2.5ST + ÜL | 14/25 | 9.1 | 61.4 | 65.4 | 6517 | 2250 | 0.386 | 0.24 | 0.35 | 215 | 7.15 | 654 | 14/25 kV (Um 30 kV)
| 3×70 + 3×35/3E + 3×2.5ST + ÜL | 14/25 | 10.8 | 65 | 69 | 7526 | 3150 | 0.272 | 0.27 | 0.33 | 265 | 10.01 | 690 | 14/25 kV (Um 30 kV)
| 3×95 + 3×50/3E + 3×2.5ST + ÜL | 14/25 | 12.7 | 70 | 73.9 | 8790 | 4275 | 0.206 | 0.3 | 0.32 | 319 | 13.59 | 739 | 14/25 kV (Um 30 kV)
| 3×120 + 3×70/3E + 3×2.5ST + ÜL | 14/25 | 14.3 | 73.9 | 77.8 | 10137 | 5400 | 0.161 | 0.33 | 0.3 | 371 | 17.16 | 778 | 14/25 kV (Um 30 kV)
| 3×150 + 3×70/3E + 3×2.5ST + ÜL | 14/25 | 16 | 78.9 | 82.8 | 11679 | 6750 | 0.129 | 0.36 | 0.29 | 428 | 21.45 | 828 | 14/25 kV (Um 30 kV)
| 3×185 + 3×95/3E + 3×2.5ST + ÜL | 14/25 | 17.7 | 82.5 | 86.4 | 13095 | 8325 | 0.106 | 0.39 | 0.29 | 488 | 26.46 | 864 | 14/25 kV (Um 30 kV)
| 3×50 + 3×25/3E + 3×2.5ST + ÜL | 18/30 | 9.1 | 67.4 | 71.4 | 7487 | 2250 | 0.386 | 0.2 | 0.37 | 215 | 7.15 | 714 | 18/30 kV (Um 36 kV)
| 3×70 + 3×35/3E + 3×2.5ST + ÜL | 18/30 | 10.8 | 71.1 | 75.1 | 8549 | 3150 | 0.272 | 0.22 | 0.35 | 265 | 10.01 | 751 | 18/30 kV (Um 36 kV)
| 3×95 + 3×50/3E + 3×2.5ST + ÜL | 18/30 | 12.7 | 76.5 | 80.4 | 10091 | 4275 | 0.206 | 0.25 | 0.34 | 319 | 13.59 | 804 | 18/30 kV (Um 36 kV)
| 3×120 + 3×70/3E + 3×2.5ST + ÜL | 18/30 | 14.3 | 79.9 | 83.8 | 11268 | 5400 | 0.161 | 0.27 | 0.33 | 371 | 17.16 | 838 | 18/30 kV (Um 36 kV)
| 3×150 + 3×70/3E + 3×2.5ST + ÜL | 18/30 | 16 | 84.4 | 89.3 | 12887 | 6750 | 0.129 | 0.29 | 0.31 | 428 | 21.45 | 893 | 18/30 kV (Um 36 kV)
Ampacity for cables laid on the floor at 30 °C ambient temperature (DIN VDE 0298-4 Table 15): 131–461 A at 3.6/6 & 6/10 kV; 139–488 A at 8.7/15 to 18/30 kV.
Ambient temperature derating factors (DIN VDE 0298-4, 90 °C conductor): 10 °C: 1.15 · 20 °C: 1.08 · 30 °C: 1.00 · 40 °C: 0.91 · 50 °C: 0.82 · 60 °C: 0.71 · 70 °C: 0.58 · 80 °C: 0.41.

## Technical data
(N)3GHSSYCY 3.6/6–18/30 kV Armoured MV Mining & Tunnel Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-3ghssycy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6–18/30 kV (6 voltage classes up to Um 36 kV)
Key data | Cross-section | 3×25–3×185 mm² (+ 3×16/3E–120/3E + 3×2.5ST + ÜL)
Key data | Conductor max | +90 °C (250 °C) (Operating +90 °C · short-circuit 250 °C)
Key data | Ambient temp. | -40 to +80 °C (Fixed -40..+80 °C · flexed +5..+60/80 °C)
Key data | Min. bend radius | 6×D / 10×D (Fixed 5–6×OD · flexed / shifting 10×OD)
Key data | Pulling load | 15 N/mm² (1,125–8,325 N max static tensile force)
Electrical | Rated voltage U0/U | 3.6/6 · 6/10 · 8.7/15 · 12/20 · 14/25 · 18/30 kV
Electrical | Max. operating voltage AC (Um) | 4.2/7.2 · 6.9/12 · 10.4/18 · 13.9/24 · 17.3/30 · 20.8/36 kV
Electrical | Max. operating voltage DC | 5.4/10.8 · 9/18 · 13.5/27 · 18/36 · 22.5/45 · 27/54 kV
Electrical | AC test voltage (5 min, main / control) | 11 · 17 · 24 · 29 · 36 · 43 kV (control cores: 2 kV)
Thermal | Max. conductor operating temperature | +90 °C
Thermal | Max. short-circuit temperature (1 s) | +250 °C
Thermal | Ambient temperature (fixed installation) | -40 °C to +80 °C
Thermal | Ambient temperature (flexed / shifting) | +5 °C to +60 °C (up to +80 °C short-term)
Mechanical | Max. permissible tensile load | 15 N/mm² on phase conductors (up to 20 N/mm² peak)
Mechanical | Minimum bending radius (fixed / flexed) | 6 × OD fixed (5 × OD min) · 10 × OD flexed
Mechanical | Permissible torsional stress & speed | ±25 °/m · max. 30 m/min shifting speed
Mechanical | Armour coverage | Galvanized steel wire braid, min. 75 % optical coverage
Resistance | Flame retardancy | IEC 60332-1-2 / DIN EN 60332-1-2 (VDE 0482-332-1-2)
Resistance | UV, ozone & moisture resistance | Ozone-, UV- and moisture-resistant; underground mine duty to DIN VDE 0118
Standards | Design standard | Based on DIN VDE 0250-605 & IEC 60502-2
Standards | Selection & installation standards | DIN VDE 0298-3 · DIN VDE 0298-4 · DIN VDE 0118
Standards | Customs HS code | 8544.60
Identification | Main & control core identification | Main cores: natural colour with black semicon layer · Control cores: black with white numbers
Identification | Outer sheath colour | Red

## Construction
(N)3GHSSYCY 3.6/6–18/30 kV Armoured MV Mining & Tunnel Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-3ghssycy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase & control conductors | Finely stranded Class 5 bare copper phase conductors (IEC 60228 / DIN VDE 0295); Class 5 bare or tinned copper interstitial control cores (3 × 2.5 mm² ST) | IEC 60228 / DIN VDE 0295 Class 5
2 | Electrical field control | Inner and outer extruded semiconductive rubber layers bonded to the phase insulation (3.6/6 kV also made with outer semiconductive layer over conductor tape) | DIN VDE 0250-605
3 | Phase core insulation | Cross-linked EPR rubber compound, high-grade 3GI3 (DIN VDE 0207-20) | DIN VDE 0207-20 (3GI3)
4 | Individual phase earth screens (/3E) | Concentric copper wire screen (or tinned copper wire braid/screen) applied individually around each MV phase core (16/3E to 120/3E) | DIN VDE 0250-605 (/3E)
5 | First inner sheath | Extruded PVC compound DMV6 / YM5 (or GM1b rubber filler bedding) over the laid-up phase and control cores | DIN VDE 0250-605 (DMV6 / YM5)
6 | Monitoring conductor (ÜL) | Conductive tape and overall concentric copper wire spinning/braid over the first inner sheath for radial earth-fault and crush monitoring | DIN VDE 0250-605 (ÜL)
7 | Second (intermediate) sheath | Extruded PVC compound DMV6 / YM5 isolating the ÜL monitoring conductor from the steel armour | DIN VDE 0250-605 (DMV6 / YM5)
8 | Mechanical armour (C) | Galvanized steel wire braid (min. 75 % coverage) over the second inner sheath | DIN VDE 0250-605 (C)
9 | Outer sheath (Y) | Heavy-duty flame-retardant PVC compound DMV6 / YM5, colour red | DIN VDE 0250-605 (DMV6 / YM5)

## Series
(N)3GHSSYCY 3.6/6–18/30 kV Armoured MV Mining & Tunnel Cable – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-3ghssycy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605. Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
3.6/6 kV | 3.6/6 kV (Um 7.2 kV)
6/10 kV | 6/10 kV (Um 12 kV)
8.7/15 kV | 8.7/15 kV (Um 18 kV)
12/20 kV | 12/20 kV (Um 24 kV)
14/25 kV | 14/25 kV (Um 30 kV)
18/30 kV | 18/30 kV (Um 36 kV)

## Quality and supply
(N)3GHSSYCY 3.6/6–18/30 kV Armoured MV Mining & Tunnel Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-3ghssycy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-605. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test on main & control cores — 11 · 17 · 24 · 29 · 36 · 43 kV AC (50 Hz, 5 min) on phase cores; 2 kV AC on control cores | Every manufactured length (DIN VDE 0250-605 / DIN VDE 0472-508)
Routine test | Conductor DC resistance & double-screen continuity — IEC 60228 Class 5 bare copper limits (DIN VDE 0472-501); 3E and ÜL screens verified continuous | Every manufactured length
Type test | Vertical flame propagation & mechanical non-electrical tests — IEC 60332-1-2 (DIN VDE 0482-332-1-2) & DIN VDE 0472-401, -402, -602, -303, -615 | Type qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)3GHSSYCY [size] [U0/U kV] VDE 0250-605 · [year] · [metre mark]
Supply | Delivery form: Standard wooden mine drums or custom cut lengths
Supply | Voltage range coverage: 3.6/6 kV, 6/10 kV, 8.7/15 kV, 12/20 kV, 14/25 kV and 18/30 kV
Supply | Minimum order: None
Supply | Lead time: None