## Request a quote
Request a quotation for (N)7YRDGOEU-J
Application engineer · reeling & crane cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-7yrdgoeu-j-0-6-1kv-etfe-epr-eva-spring-reeling-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
(N)7YRDGOEU-J 0.6/1 kV ETFE/EPR/EVA Spring-Reeling Cable – Dimensions, tensile ratings & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-7yrdgoeu-j-0-6-1kv-etfe-epr-eva-spring-reeling-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on DIN VDE 0250-814 / IEC 60228. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Tensile load kN ≈ | Min. bend R mm | Series
| (N)7YRDGOEU-J 4G2.5 | 4G2.5 mm² | Class FS extra-fine Cu | 11.2 | 195 | 1.2 | 70 | (N)7YRDGOEU-J Construction Schedule (−40…+90 °C)
| (N)7YRDGOEU-J 4G4 | 4G4 mm² | Class FS extra-fine Cu | 12.8 | 265 | 1.9 | 80 | (N)7YRDGOEU-J Construction Schedule (−40…+90 °C)
| (N)7YRDGOEU-J 4G6 | 4G6 mm² | Class FS extra-fine Cu | 14.4 | 355 | 2.8 | 90 | (N)7YRDGOEU-J Construction Schedule (−40…+90 °C)
| (N)7YRDGOEU-J 7G2.5 | 7G2.5 mm² | Class FS extra-fine Cu | 14.1 | 310 | 2.1 | 85 | (N)7YRDGOEU-J Construction Schedule (−40…+90 °C)
| (N)7YRDGOEU-J 12G1.5 | 12G1.5 mm² | Class FS extra-fine Cu | 15.6 | 365 | 2.2 | 95 | (N)7YRDGOEU-J Construction Schedule (−40…+90 °C)
Custom core counts, cross-sections, sheath colours and factory-tested cut lengths available per DIN VDE 0250-814 / IEC 60228.

## Electrical, optical & thermal p
(N)7YRDGOEU-J 0.6/1 kV ETFE/EPR/EVA Spring-Reeling Cable – Electrical, optical & thermal parameters (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-7yrdgoeu-j-0-6-1kv-etfe-epr-eva-spring-reeling-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on DIN VDE 0250-814 / IEC 60228. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Capacity | Operating temp.
4G2.5 mm² | 7.98 | 0.6/1 kV / 26 A | −40…+90 °C
4G4 mm² | 4.95 | 0.6/1 kV / 34 A | −40…+90 °C
4G6 mm² | 3.3 | 0.6/1 kV / 44 A | −40…+90 °C
7G2.5 mm² | 7.98 | 0.6/1 kV / 20 A | −40…+90 °C
12G1.5 mm² | 13.3 | 0.6/1 kV / 13 A | −40…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric and dimensional verification.

## Technical data
(N)7YRDGOEU-J 0.6/1 kV ETFE/EPR/EVA Spring-Reeling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-7yrdgoeu-j-0-6-1kv-etfe-epr-eva-spring-reeling-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on DIN VDE 0250-814 / IEC 60228. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U AC (1.2 kV max AC))
Key data | Operating temp. | −40…+90 °C (Continuous thermal operating range)
Key data | Min. bend radius | 6–10 × OD (Installed / dynamic routing limit)
Key data | Core / conductor | Class FS Cu (Extra-fine bare copper strands)
Key data | Outer protection | EVA Elastomer (Crosslinked EVA + torsion braid)
Key data | Standard | VDE 0250-814 (DIN VDE 0250-814 / IEC 60228)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (DIN VDE 0250-814 / IEC 60228)
Electrical | Core / conductor construction | Extra-Fine Conductors (4G4 mm²) — Class FS extra-finely stranded plain annealed copper conductors engineered for compact spring-operated reeling drums
Electrical | Primary dielectric / insulation | ETFE Core Insulation (7Y) — High-strength extruded ethylene tetrafluoroethylene (ETFE) fluoropolymer core insulation (numbered black cores + green/yellow PE)
Thermal | Continuous operating temperature | −40…+90 °C (rated operating envelope)
Thermal | Storage & transport temperature | −40…+80 °C on export drum or reel
Mechanical | Outer protection / sheath | EVA Outer Sheath — Heavy-duty crosslinked ethylene vinyl acetate (EVA) outer jacket resistant to oil, ozone, UV, and mechanical abrasion
Mechanical | Minimum bending radius | 6–10 × OD
Mechanical | Structural layer count | 5 concentric functional layers
Resistance | Environmental & chemical resistance | Industrial moisture, oils and mechanical wear per DIN VDE 0250-814 / IEC 60228
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0250-814 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | (N)7YRDGOEU-J
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
(N)7YRDGOEU-J 0.6/1 kV ETFE/EPR/EVA Spring-Reeling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-7yrdgoeu-j-0-6-1kv-etfe-epr-eva-spring-reeling-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on DIN VDE 0250-814 / IEC 60228. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Extra-Fine Conductors (4G4 mm²) | Class FS extra-finely stranded plain annealed copper conductors engineered for compact spring-operated reeling drums | DIN VDE 0250-814 / IEC 60228
2 | ETFE Core Insulation (7Y) | High-strength extruded ethylene tetrafluoroethylene (ETFE) fluoropolymer core insulation (numbered black cores + green/yellow PE) | DIN VDE 0250-814 / IEC 60228
3 | Inner Elastomeric Sheath | Extruded black special ethylene propylene rubber (EPR) inner bedding sheath stabilizing the core lay under reeling tension | DIN VDE 0250-814 / IEC 60228
4 | Anti-Torsion Braid | High-tenacity synthetic textile anti-torsion reinforcement braid vulkanized between inner and outer elastomeric sheaths | DIN VDE 0250-814 / IEC 60228
5 | EVA Outer Sheath | Heavy-duty crosslinked ethylene vinyl acetate (EVA) outer jacket resistant to oil, ozone, UV, and mechanical abrasion | DIN VDE 0250-814 / IEC 60228
| (N)7YRDGOEU-J — Standard Execution | Built to DIN VDE 0250-814 / IEC 60228 with extra-fine conductors (4g4 mm²) and eva outer sheath
| (N)7YRDGOEU-J — Custom Length & Configuration | Available in custom drum lengths, core counts or factory-terminated assemblies
| (N)7YRDGOEU-J — Factory Routine Certified | Supplied with EN 10204 3.1 routine electrical, dielectric & dimensional inspection report

## Quality and supply
(N)7YRDGOEU-J 0.6/1 kV ETFE/EPR/EVA Spring-Reeling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-7yrdgoeu-j-0-6-1kv-etfe-epr-eva-spring-reeling-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on DIN VDE 0250-814 / IEC 60228. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance & dimensional verification (DIN VDE 0250-814 / IEC 60228) — Electrical parameters and outer diameter within DIN VDE 0250-814 / IEC 60228 tolerances | Every manufactured drum / length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0250-814 / IEC 60228) — Zero dielectric breakdown and verified insulation resistance over full length | Every manufactured drum / length
Type test | Thermal ageing, mechanical flexing & environmental qualification (DIN VDE 0250-814 / IEC 60228) — Verified structural and dielectric integrity across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0250-814 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)7YRDGOEU-J VDE 0250-814 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export wooden/steel drums or factory-tested coils
Supply | Standard lengths: 100 m, 250 m, 500 m, 1,000 m or custom cut-to-length reels
Supply | MOQ: 100 m (standard configurations) · 300 m (custom builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP