## Request a quote
Request a quotation for (N)GRDGCGÖU
Application engineer · crane & chain cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-grdgcgoeu-screened-energy-chain-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)GRDGCGÖU 0.6/1 kV Screened Energy-Chain & Crane Festoon Cable – Dimensions & weights (34)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-grdgcgoeu-screened-energy-chain-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-814. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Construction | Cond. Ø mm | OD min mm | OD max mm | Min. bend R mm | Weight ≈ kg/km | Max. pull N | Max. R20 Ω/km | Series
| (N)GRDGCGÖU-O 1×16C | 1 × 16C | 5.7 | 10.1 | 12.1 | 61 | 320 | 240 | 1.21 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×25C | 1 × 25C | 7.1 | 12.8 | 14.8 | 74 | 450 | 370 | 0.78 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×35C | 1 × 35C | 8.3 | 13.7 | 15.7 | 79 | 540 | 520 | 0.55 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×50C | 1 × 50C | 9.8 | 15.7 | 17.7 | 89 | 740 | 750 | 0.39 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×70C | 1 × 70C | 11.6 | 18.7 | 20.7 | 104 | 1020 | 1050 | 0.27 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×95C | 1 × 95C | 13.8 | 20.8 | 22.8 | 114 | 1260 | 1420 | 0.21 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×120C | 1 × 120C | 14.9 | 22.8 | 24.8 | 124 | 1580 | 1800 | 0.16 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×150C | 1 × 150C | 17.2 | 25.6 | 28.6 | 143 | 2000 | 2250 | 0.13 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×185C | 1 × 185C | 18 | 27.7 | 30.7 | 154 | 2370 | 2770 | 0.11 | Single-core 16–240C
| (N)GRDGCGÖU-O 1×240C | 1 × 240C | 22.5 | 31.9 | 34.9 | 175 | 3130 | 3600 | 0.08 | Single-core 16–240C
| (N)GRDGÖU-J 4G2.5 | 4 × 2.5 | 2 | 9.9 | 11.5 | 46 | 200 | 150 | 7.98 | Unscreened 4-core
| (N)GRDGÖU-J 4G4 | 4 × 4 | 2.9 | 12.7 | 14.7 | 74 | 320 | 240 | 4.95 | Unscreened 4-core
| (N)GRDGÖU-J 4G6 | 4 × 6 | 3.6 | 14.2 | 16.2 | 81 | 430 | 360 | 3.3 | Unscreened 4-core
| (N)GRDGÖU-J 4G10 | 4 × 10 | 4.6 | 16.7 | 18.7 | 94 | 670 | 600 | 1.91 | Unscreened 4-core
| (N)GRDGÖU-J 4G16 | 4 × 16 | 5.9 | 21.2 | 23.2 | 116 | 1020 | 960 | 1.21 | Unscreened 4-core
| (N)GRDGÖU-J 4G25 | 4 × 25 | 7.2 | 26.5 | 29.5 | 148 | 1600 | 1500 | 0.78 | Unscreened 4-core
| (N)GRDGCGÖU-J 3×35+3G16/3 | 3 × 35 + 3G16/3 | 8.1 | 26.4 | 29.4 | 147 | 1770 | 1570 | 0.55 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 3×50+3G25/3 | 3 × 50 + 3G25/3 | 10 | 31.5 | 34.5 | 173 | 2560 | 2250 | 0.39 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 3×70+3G35/3 | 3 × 70 + 3G35/3 | 11.9 | 37.6 | 40.6 | 203 | 3550 | 3150 | 0.27 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 4G2.5C | 4 × 2.5C | 1.9 | 11.2 | 13.2 | 66 | 310 | 150 | 7.98 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 4G4C | 4 × 4C | 2.9 | 15.2 | 17.2 | 86 | 490 | 240 | 4.95 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 4G6C | 4 × 6C | 3.6 | 17 | 19 | 95 | 650 | 360 | 3.3 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 4G10C | 4 × 10C | 4.6 | 19.2 | 21.2 | 106 | 870 | 600 | 1.91 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 3×16+3G2.5C | 3 × 16 + 3G2.5C | 5.9 | 20.3 | 22.3 | 112 | 1050 | 720 | 1.21 | Screened VFD 3+3 & 4C
| (N)GRDGCGÖU-J 3×25+3G4C | 3 × 25 + 3G4C | 7.2 | 25.7 | 28.7 | 144 | 1610 | 1120 | 0.78 | Screened VFD 3+3 & 4C
| (N)GRDGÖU-J 12G1.5 | 12 × 1.5 | 1.5 | 11.7 | 13.7 | 69 | 305 | 270 | 13.3 | Control 7–24 cores
| (N)GRDGÖU-J 24G1.5 | 24 × 1.5 | 1.5 | 19.9 | 21.9 | 110 | 710 | 540 | 13.3 | Control 7–24 cores
| (N)GRDGÖU-J 7G2.5 | 7 × 2.5 | 1.9 | 11.3 | 13.3 | 67 | 290 | 260 | 7.98 | Control 7–24 cores
| (N)GRDGÖU-J 12G2.5 | 12 × 2.5 | 1.9 | 15.3 | 17.4 | 87 | 490 | 450 | 7.98 | Control 7–24 cores
| (N)GRDGÖU-J 18G2.5 | 18 × 2.5 | 1.9 | 19.5 | 21.5 | 108 | 760 | 670 | 7.98 | Control 7–24 cores
| (N)GRDGÖU-J 24G2.5 | 24 × 2.5 | 1.9 | 22.5 | 24.5 | 123 | 1020 | 900 | 7.98 | Control 7–24 cores
| (N)GRDGCGÖU-O 1×(2×0.5)C | 1 × (2 × 0.5)C | 0.9 | 8 | 10 | 40 | 135 | 10 | 39 | Screened bus pairs
| (N)GRDGCGÖU-O 4×(2×0.5)C | 4 × (2 × 0.5)C | 0.9 | 17.6 | 19.6 | 98 | 500 | 60 | 39 | Screened bus pairs
| (N)GRDGCGÖU-O 4×(2×1)C | 4 × (2 × 1)C | 1.3 | 26.3 | 29.3 | 147 | 1130 | 180 | 19.5 | Screened bus pairs
Configurations with suffix 'C' or '/3' include the tinned copper braid EMC screen; unscreened companion power/control sizes share the same EPR/EVA chain-optimized jacket.

## Ampacity & short-circuit data
(N)GRDGCGÖU 0.6/1 kV Screened Energy-Chain & Crane Festoon Cable – Ampacity & short-circuit data (17)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-grdgcgoeu-screened-energy-chain-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-814. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. R20 Ω/km | Current rating in air 30 °C, A | Short-circuit 1 s kA
0.5 | 20 | 39 | 10 | 0.07
1.0 | 18 | 19.5 | 19 | 0.14
1.5 | 16 | 13.3 | 23 | 0.21
2.5 | 14 | 7.98 | 30 | 0.36
4 | 12 | 4.95 | 41 | 0.57
6 | 10 | 3.3 | 53 | 0.86
10 | 8 | 1.91 | 74 | 1.43
16 | 6 | 1.21 | 99 | 2.29
25 | 4 | 0.78 | 131 | 3.58
35 | 2 | 0.55 | 162 | 5.01
50 | 1 | 0.39 | 202 | 7.15
70 | 2/0 | 0.27 | 250 | 10.01
95 | 3/0 | 0.21 | 301 | 13.59
120 | 4/0 | 0.16 | 352 | 17.16
150 | 300 kcmil | 0.13 | 404 | 21.45
185 | 350 kcmil | 0.11 | 461 | 26.46
240 | 500 kcmil | 0.08 | 546 | 34.32
Current ratings apply at 30 °C ambient in free air per DIN VDE 0298-4; apply grouping derating when multiple power cables are bundled in the same energy chain.

## Technical data
(N)GRDGCGÖU 0.6/1 kV Screened Energy-Chain & Crane Festoon Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-grdgcgoeu-screened-energy-chain-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-814. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U · max. AC 0.7/1.2 kV)
Key data | EMC screen | TCWB > 80% (Z_T < 100 mΩ/m at 30 MHz)
Key data | Travel speed | 240 m/min (Long-travel crane energy chains)
Key data | Bending radius | 5 × D (Dynamic chain & festoon service)
Key data | Flexing temp. | -35 to +80 °C (Mobile · -50 to +80 °C fixed)
Key data | Max. conductor | +90 °C (250 °C short-circuit (≤ 5 s))
Electrical | Rated voltage U0/U | 0.6/1 kV (max. AC 0.7/1.2 kV · DC 0.9/1.8 kV)
Electrical | AC test voltage | 3.5 kV (5 min)
Electrical | EMC screen & transfer impedance | Tinned copper braid (> 80 % coverage) · Transfer impedance < 100 mΩ/m at 30 MHz
Thermal | Max. conductor operating temperature | +90 °C
Thermal | Max. short-circuit temperature (≤ 5 s) | +250 °C
Thermal | Ambient temperature — flexing / mobile | -35 to +80 °C
Thermal | Ambient temperature — fixed installation | -50 to +80 °C
Mechanical | Max. travel speed | Up to 240 m/min in energy chains and festoon systems
Mechanical | Max. tensile load & torsion | 15 N/mm² max. tensile load · Torsional stress not allowed
Mechanical | Min. bending radius | Acc. to DIN VDE 0298-3
Standards | Reference standards | DIN VDE 0250-814 (VDE Reg. 7841) · DIN VDE 0298-3/-4 · IEC 60228 Class 5
Standards | Chemical & fire performance | Halogen-free · Oil-resistant EN 60811-404 · UV, ozone & abrasion resistant EVA sheath

## Construction
(N)GRDGCGÖU 0.6/1 kV Screened Energy-Chain & Crane Festoon Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-grdgcgoeu-screened-energy-chain-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-814. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductor | Finely stranded bare electrolytic copper, Class 5 (split earth conductors Class FS) | IEC 60228 / DIN VDE 0295 Class 5
2 | Core insulation | High-grade special EPR elastomer compound (3GI3); ETFE option on control cores
3 | Inner sheath | Pressure-extruded EPR rubber inner sheath (GM1b)
4 | EMC copper braid screen | Tinned copper wire braid over inner sheath (> 80 % optical coverage) | Surface transfer impedance < 100 mΩ/m at 30 MHz
5 | Outer sheath | Abrasion-resistant halogen-free EVA / special elastomer outer sheath, black
| 1×16C – 1×240C | Screened single-core VFD power leads for high-current crane drives
| 3×..+3G../3 & 4G..C | Symmetrical 3+3 split-earth and 4-core screened VFD motor cables
| 1×(2×0.5)C – 4×(2×1)C | Screened twisted-pair data and fieldbus cables for energy chains

## Quality and supply
(N)GRDGCGÖU 0.6/1 kV Screened Energy-Chain & Crane Festoon Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-grdgcgoeu-screened-energy-chain-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-814. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 3.5 kV, 5 min | Every length
Routine test | Conductor resistance — IEC 60228 / DIN VDE 0295 Class 5 | Every length
Type test | Transfer impedance at 30 MHz — < 100 mΩ/m (> 80 % braid coverage) | Type approval
Type test | Oil & environmental resistance — EN 60811-404 · Halogen-free | Per compound batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)GRDGCGÖU 3x35+3G16/3 0.6/1 kV DIN VDE 0250-814 · CE · [year] · [metre mark]
Supply | Standard packing: 500 m / 1,000 m on wooden drums or custom chain lengths
Supply | HS code: 8544.49
Supply | Minimum order: None
Supply | Lead time: None