## Request a quote
Request a quotation for (N)SHÖU
Application engineer · VDE 0250-812 mining & industrial rubber cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-shoeu-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)SHÖU 0.6/1 kV Flexible Mining & Industrial Rubber Cable – Dimensions & mechanical loads (80 configs) (80)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores | Cross-section | Cond. Ø | Outer Ø min | Outer Ø max | Weight ≈ | Max. pull | Min. bend R (5×D) | Current 30 °C | Series
| (N)SHÖU-O 1 × 16 | 1 | 16 | 5.2 | 9.5 | 11.1 | 230 | 240 | 56 | 99 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 25 | 1 | 25 | 6.4 | 11 | 12.6 | 335 | 375 | 63 | 131 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 35 | 1 | 35 | 7.5 | 12.3 | 13.9 | 435 | 525 | 70 | 162 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 50 | 1 | 50 | 9 | 14.5 | 16.5 | 615 | 750 | 82 | 202 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 70 | 1 | 70 | 11.1 | 16.4 | 18.4 | 830 | 1050 | 92 | 250 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 95 | 1 | 95 | 12.8 | 18.5 | 20.5 | 1060 | 1425 | 102 | 301 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 120 | 1 | 120 | 14.5 | 20.4 | 22.4 | 1300 | 1800 | 112 | 352 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 150 | 1 | 150 | 16.5 | 22.8 | 24.8 | 1600 | 2250 | 124 | 404 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 185 | 1 | 185 | 17.9 | 24.7 | 27.7 | 2020 | 2775 | 138 | 461 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 240 | 1 | 240 | 21.2 | 27.6 | 30.6 | 2548 | 3600 | 153 | 540 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 1 × 300 | 1 | 300 | 23.6 | 31.6 | 34.6 | 3200 | 4500 | 173 | 620 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 2 × 1.5 | 2 | 1.5 | 1.6 | 9.8 | 11.4 | 150 | 45 | 57 | 23 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 2 × 2.5 | 2 | 2.5 | 2 | 10.7 | 12.3 | 185 | 75 | 62 | 30 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-O 2 × 4 | 2 | 4 | 2.4 | 11.9 | 13.5 | 220 | 120 | 68 | 41 | 1-Core & 2-Core (N)SHÖU-O
| (N)SHÖU-J 3 × 1.5 | 3 | 1.5 | 1.5 | 9.7 | 10.3 | 141 | 68 | 52 | 24 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-J 3 × 2.5 | 3 | 2.5 | 1.9 | 11.1 | 12.7 | 210 | 113 | 64 | 30 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-J 3 × 4 | 3 | 4 | 2.4 | 12.1 | 13.8 | 290 | 180 | 69 | 41 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-J 3 × 6 | 3 | 6 | 2.9 | 13.2 | 15 | 360 | 270 | 75 | 53 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 10 | 3 | 10 | 3.8 | 16.1 | 18.5 | 590 | 450 | 92 | 74 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 16 | 3 | 16 | 4.8 | 19 | 21 | 797 | 720 | 105 | 99 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 25 | 3 | 25 | 6.1 | 22.9 | 24.9 | 1206 | 1125 | 124 | 131 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 35 | 3 | 35 | 7.2 | 24.9 | 27.9 | 1649 | 1575 | 140 | 162 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 50 | 3 | 50 | 8.9 | 29.4 | 33 | 2195 | 2250 | 165 | 202 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 70 | 3 | 70 | 10.6 | 34.8 | 37.8 | 3124 | 3150 | 189 | 250 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 95 | 3 | 95 | 12.3 | 40.9 | 43.9 | 4100 | 4275 | 220 | 301 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 120 | 3 | 120 | 13.8 | 43.4 | 47.7 | 4723 | 5400 | 238 | 352 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 150 | 3 | 150 | 15.5 | 47.8 | 54 | 5916 | 6750 | 270 | 404 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-O 3 × 185 | 3 | 185 | 17 | 53.1 | 58.6 | 7271 | 8325 | 293 | 461 | 3-Core (N)SHÖU-O / -J
| (N)SHÖU-J 4 × 1.5 | 4 | 1.5 | 1.5 | 10.5 | 12.6 | 200 | 90 | 63 | 24 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 2.5 | 4 | 2.5 | 1.9 | 12 | 13.6 | 270 | 150 | 68 | 30 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 4 | 4 | 4 | 2.4 | 13 | 14.9 | 356 | 240 | 74 | 41 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 6 | 4 | 6 | 2.9 | 14.9 | 16.9 | 459 | 360 | 84 | 53 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 10 | 4 | 10 | 3.8 | 17.4 | 20.2 | 690 | 600 | 101 | 74 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 16 | 4 | 16 | 4.8 | 21 | 23.1 | 1038 | 960 | 116 | 99 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 25 | 4 | 25 | 6.1 | 24.5 | 28.1 | 1576 | 1500 | 140 | 131 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 35 | 4 | 35 | 7.2 | 28.4 | 31.4 | 2078 | 2100 | 157 | 162 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 50 | 4 | 50 | 8.9 | 33.6 | 36.6 | 2967 | 3000 | 183 | 202 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 70 | 4 | 70 | 10.6 | 38.8 | 42.5 | 3931 | 4200 | 212 | 250 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 95 | 4 | 95 | 12.3 | 44.8 | 47.8 | 5165 | 5700 | 239 | 301 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 120 | 4 | 120 | 13.8 | 49.8 | 53.8 | 6200 | 7200 | 269 | 352 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 150 | 4 | 150 | 15.5 | 54.9 | 58.9 | 7537 | 9000 | 294 | 404 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 4 × 185 | 4 | 185 | 17 | 61 | 63.3 | 9420 | 11100 | 316 | 461 | 4-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 1.5 | 5 | 1.5 | 1.5 | 11.4 | 13.5 | 234 | 113 | 68 | 24 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 2.5 | 5 | 2.5 | 1.9 | 12.9 | 14.6 | 318 | 188 | 73 | 30 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 4 | 5 | 4 | 2.4 | 14.7 | 16.7 | 434 | 300 | 84 | 41 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 6 | 5 | 6 | 2.9 | 16.1 | 18.6 | 594 | 450 | 93 | 53 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 10 | 5 | 10 | 3.8 | 19 | 22 | 820 | 750 | 110 | 74 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 16 | 5 | 16 | 4.8 | 22.8 | 25.2 | 1283 | 1200 | 126 | 99 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 25 | 5 | 25 | 6.1 | 28 | 31 | 1880 | 1875 | 155 | 131 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 5 × 35 | 5 | 35 | 7.5 | 34.5 | 37.5 | 2650 | 2625 | 188 | 162 | 5-Core (N)SHÖU-J
| (N)SHÖU-J 3 × 50 + 3 × 25/3E | 3 | 50 + 3×25/3E | 9 | 29.4 | 33.5 | 2481 | 2250 | 168 | 202 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 70 + 3 × 35/3E | 3 | 70 + 3×35/3E | 10.6 | 35.1 | 38.1 | 3319 | 3150 | 190 | 250 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 95 + 3 × 50/3E | 3 | 95 + 3×50/3E | 12.8 | 40.7 | 43.7 | 4324 | 4275 | 218 | 301 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 120 + 3 × 70/3E | 3 | 120 + 3×70/3E | 14.4 | 44.5 | 47.5 | 5476 | 5400 | 238 | 352 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 150 + 3 × 70/3E | 3 | 150 + 3×70/3E | 16.5 | 49.5 | 55.6 | 6950 | 6750 | 278 | 404 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 185 + 3 × 95/3E | 3 | 185 + 3×95/3E | 17.9 | 54.5 | 58.5 | 8298 | 8325 | 292 | 461 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 240 + 3 × 120/3E | 3 | 240 + 3×120/3E | 20.6 | 60.9 | 66.2 | 10700 | 10800 | 331 | 540 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 3 × 300 + 3 × 150/3E | 3 | 300 + 3×150/3E | 23.4 | 70.3 | 74.3 | 13300 | 13500 | 372 | 620 | 3+3 Split-Earth (N)SHÖU-J
| (N)SHÖU-J 7 × 1.5 | 7 | 1.5 | 1.6 | 12.9 | 15.1 | 300 | 158 | 76 | 16 | Control & Screened KON
| (N)SHÖU-J 8 × 1.5 | 8 | 1.5 | 1.6 | 13.8 | 15.4 | 325 | 180 | 77 | 15 | Control & Screened KON
| (N)SHÖU-J 10 × 1.5 | 10 | 1.5 | 1.6 | 15.5 | 17.5 | 400 | 225 | 88 | 13 | Control & Screened KON
| (N)SHÖU-J 12 × 1.5 | 12 | 1.5 | 1.6 | 15.8 | 17.8 | 422 | 270 | 89 | 12 | Control & Screened KON
| (N)SHÖU-J 14 × 1.5 | 14 | 1.5 | 1.6 | 16.8 | 18.8 | 495 | 315 | 94 | 12 | Control & Screened KON
| (N)SHÖU-J 18 × 1.5 | 18 | 1.5 | 1.6 | 18.5 | 20.5 | 610 | 405 | 102 | 11 | Control & Screened KON
| (N)SHÖU-J 19 × 1.5 | 19 | 1.5 | 1.6 | 18.9 | 20.9 | 650 | 428 | 104 | 11 | Control & Screened KON
| (N)SHÖU-J 24 × 1.5 | 24 | 1.5 | 1.6 | 20 | 22 | 752 | 540 | 110 | 10 | Control & Screened KON
| (N)SHÖU-J 7 × 2.5 | 7 | 2.5 | 2 | 14.9 | 17.4 | 458 | 263 | 87 | 20 | Control & Screened KON
| (N)SHÖU-J 8 × 2.5 | 8 | 2.5 | 2 | 15.8 | 17.8 | 480 | 300 | 89 | 19 | Control & Screened KON
| (N)SHÖU-J 10 × 2.5 | 10 | 2.5 | 2 | 16.4 | 18.4 | 500 | 375 | 92 | 17 | Control & Screened KON
| (N)SHÖU-J 12 × 2.5 | 12 | 2.5 | 2 | 18 | 20.6 | 653 | 450 | 103 | 16 | Control & Screened KON
| (N)SHÖU-J 15 × 2.5 | 15 | 2.5 | 2 | 20.7 | 22.7 | 780 | 563 | 114 | 15 | Control & Screened KON
| (N)SHÖU-J 18 × 2.5 | 18 | 2.5 | 2 | 21.2 | 24.4 | 900 | 675 | 122 | 14 | Control & Screened KON
| (N)SHÖU-J 19 × 2.5 | 19 | 2.5 | 2 | 22.3 | 24.3 | 900 | 713 | 122 | 14 | Control & Screened KON
| (N)SHÖU-J 24 × 2.5 | 24 | 2.5 | 2 | 22.8 | 26.3 | 1140 | 900 | 132 | 12 | Control & Screened KON
| (N)SHÖU-J 37 × 2.5 | 37 | 2.5 | 2 | 29 | 31 | 1600 | 1388 | 155 | 10 | Control & Screened KON
| (N)SHÖU-J 7 × 1.5 / 4 KON | 7 | 1.5 + 4 KON | 1.6 | 15.5 | 17.5 | 360 | 158 | 88 | 16 | Control & Screened KON
| (N)SHÖU-J 12 × 1.5 / 4 KON | 12 | 1.5 + 4 KON | 1.6 | 18 | 20 | 517 | 270 | 100 | 12 | Control & Screened KON
| (N)SHÖU-J 18 × 1.5 / 1.5 KON | 18 | 1.5 + 1.5 KON | 1.6 | 22 | 24 | 720 | 405 | 120 | 11 | Control & Screened KON
| (N)SHÖU-J 7 × 2.5 / 2.5 KON | 7 | 2.5 + 2.5 KON | 2 | 14 | 15.6 | 418 | 263 | 78 | 20 | Control & Screened KON
| (N)SHÖU-J 12 × 2.5 / 2.5 KON | 12 | 2.5 + 2.5 KON | 2 | 16 | 18 | 630 | 450 | 90 | 16 | Control & Screened KON
Permissible continuous tensile load is 15 N/mm² of active phase conductor cross-section per DIN VDE 0298-3.
In 3+3 split-earth constructions (50 to 300 mm²), the protective earth conductor is divided into three symmetrical interstitial conductors (e.g. 3 × 50 + 3 × 25/3E) to reduce overall diameter and improve bending symmetry on drill and LHD reels.
Current ratings shown are for cables laid on the floor at 30 °C ambient (DIN VDE 0298-4 Table 15); for 7–37 core control cables, DIN VDE 0298-4 multicore grouping factors (0.65 down to 0.35) are applied.

## Ampacity, reel derating & volta
(N)SHÖU 0.6/1 kV Flexible Mining & Industrial Rubber Cable – Ampacity, reel derating & voltage drop (1.5–300 mm²) (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Conductor | Max. DC R (20 °C) | On floor | Free air | Reel 1L | Reel 2L | Reel 3L | ΔU cosφ 0.8 | ΔU cosφ 1.0 | 1 s Isc
1.5 mm² | 13.3 | 24 | 25 | 19 | 15 | 12 | 23.56 | 29.32 | 0.18
2.5 mm² | 7.98 | 30 | 32 | 24 | 18 | 15 | 14.17 | 17.59 | 0.31
4 mm² | 4.95 | 41 | 43 | 33 | 25 | 20 | 8.82 | 10.92 | 0.57
6 mm² | 3.3 | 53 | 56 | 42 | 32 | 26 | 5.9 | 7.27 | 0.86
10 mm² | 1.91 | 74 | 78 | 59 | 45 | 36 | 3.44 | 4.2 | 1.43
16 mm² | 1.21 | 99 | 104 | 79 | 60 | 49 | 2.21 | 2.66 | 2.29
25 mm² | 0.78 | 131 | 138 | 105 | 80 | 64 | 1.45 | 1.71 | 3.58
35 mm² | 0.554 | 162 | 170 | 130 | 99 | 79 | 1.06 | 1.23 | 5.01
50 mm² | 0.386 | 202 | 212 | 162 | 123 | 99 | 0.77 | 0.87 | 7.15
70 mm² | 0.272 | 250 | 263 | 200 | 153 | 123 | 0.56 | 0.61 | 10.01
95 mm² | 0.206 | 301 | 316 | 241 | 184 | 147 | 0.45 | 0.47 | 13.59
120 mm² | 0.161 | 352 | 370 | 282 | 215 | 172 | 0.36 | 0.36 | 17.16
150 mm² | 0.129 | 404 | 424 | 323 | 246 | 198 | 0.31 | 0.29 | 21.45
185 mm² | 0.106 | 461 | 484 | 369 | 281 | 226 | 0.27 | 0.24 | 26.46
240 mm² | 0.0801 | 528 | 554 | 422 | 322 | 259 | 0.22 | 0.18 | 34.32
300 mm² | 0.0641 | 620 | 651 | 496 | 378 | 304 | 0.19 | 0.15 | 42.9
Ambient temperature derating factors (base 30 °C = 1.00, 90 °C max conductor): 10 °C: 1.15 · 15 °C: 1.12 · 20 °C: 1.08 · 25 °C: 1.04 · 30 °C: 1.00 · 35 °C: 0.96 · 40 °C: 0.91 · 45 °C: 0.87 · 50 °C: 0.82 · 55 °C: 0.76 · 60 °C: 0.71 · 65 °C: 0.65 · 70 °C: 0.58 · 75 °C: 0.50 · 80 °C: 0.41.
Multicore loading derating factors (DIN VDE 0298-4): 5 loaded cores: 0.75 · 7 cores: 0.65 · 10 cores: 0.55 · 14 cores: 0.50 · 19 cores: 0.45 · 24 cores: 0.40.

## Technical data
(N)SHÖU 0.6/1 kV Flexible Mining & Industrial Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U 0.6/1 kV · max 0.7/1.2 kV AC)
Key data | Configurations | -O/-J · 3E · KON (1C–37C, 3+3E split PE & KON screen)
Key data | Min. bend radius | 4–5 × OD (4 × D fixed · 5 × D free flexing)
Key data | Ambient temp. | −25…+80 °C (−40…+80 °C fixed (90 °C cond.))
Key data | Tensile rating | 15 N/mm² (45 to 13,500 N (up to 60 m/min))
Key data | Range | 80 configs (1 × 16 to 3 × 300+3 × 150/3E mm²)
Electrical | Rated voltage U0/U | U0/U = 0.6/1 kV (600/1000 V AC)
Electrical | Max. operating voltage | 0.7/1.2 kV AC · 0.9/1.8 kV DC (DIN VDE 0298-3)
Electrical | AC test voltage | 3.0–3.5 kV AC (5 min) on main cores · 2.0 kV AC on control cores
Electrical | Current rating (30 °C) | 23 to 620 A laid on floor · 25 to 638 A in free air at 30 °C (DIN VDE 0298-4 Table 15)
Electrical | Screening options | Unscreened (-O / -J / 3E split earth) or closed concentric copper wire spinning over core assembly (...KON control types)
Thermal | Ambient temperature, flexing | −25 °C to +80 °C (continuous full-flexing operation −25 °C to +60 °C per DIN VDE 0298-3)
Thermal | Ambient temperature, fixed | −40 °C to +80 °C
Thermal | Max. conductor & short-circuit temp. | +90 °C continuous · +250 °C short-circuit (5 s)
Thermal | Submersible water rating | Up to +40 °C water temperature · up to 500 m submersion depth (EN 50525-2-21)
Mechanical | Max. permissible tensile load | 15 N/mm² of total phase conductor cross-section (45 N on 2×1.5 mm² up to 13,500 N on 3×300 mm²)
Mechanical | Minimum bending radius | 4 × D fixed installation · 5 × D free flexing (DIN VDE 0298-3 Table 3)
Mechanical | Max. reeling / drum-car speed | Up to 60 m/min on drum cars, drills & LHD reels
Mechanical | Permissible torsional stress | ±100 °/m (MT trailing/conveyor) · ±25 °/m (M+ LHD reel)
Resistance | Oil, ozone & weather resistance | Oil-resistant per IEC 60811-404 / DIN VDE 0473-811-2-1; ozone, UV, moisture & weather resistant for unrestricted indoor/outdoor use
Resistance | Flame retardance | Flame-retardant per IEC 60332-1-2 / EN 60332-1-2 / DIN VDE 0482-332-1-2
Standards | Design & application standards | DIN VDE 0250-812 & DIN VDE 0250-1 (selection & installation per DIN VDE 0298-3 & 0298-4)
Standards | Conductor standard | IEC 60228 / EN 60228 / DIN VDE 0295 Class 5 finely stranded plain or tinned electrolytic copper
Standards | Certifications & compliance | VDE certificate with factory surveillance · Low Voltage Directive 2014/35/EU · RoHS & REACH compliant

## Construction
(N)SHÖU 0.6/1 kV Flexible Mining & Industrial Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Class 5 copper conductor | Finely stranded annealed plain or tinned electrolytic copper, Class 5 per DIN VDE 0295 / IEC 60228
2 | Core insulation (3GI3 EPR) | Cross-linked ethylene-propylene elastomer (EPR) compound type 3GI3
3 | Inner sheath (EPR elastomer) | Extruded cross-linked EPR / elastomeric compound filling core interstices
4 | Concentric copper screen (...KON control types only) | Closed helical spinning of copper wires over the laid-up core assembly on (N)SHÖU-J ...KON control cables
5 | Outer sheath (5GM5 CM/CR rubber) | Heavy-duty cross-linked chlorinated rubber (CM / PCP) compound type 5GM5, yellow or black
| (N)SHÖU-O / -J Power & Multicore (1C–5C) | Single-core (16–300 mm²), 2-core (1.5–4 mm²), 3-core (1.5–185 mm²), 4-core (1.5–185 mm²) & 5-core (1.5–35 mm²) power cables
| (N)SHÖU-J 3+3E Split-Earth (MT / M+ Series) | 3 phase cores (50–300 mm²) + 3 symmetrical interstitial earth cores (25/3E–150/3E) for drills, LHDs & shiftable mining feeders
| (N)SHÖU-J Control & ...KON Screened Control (7C–37C) | Unscreened (7×1.5 to 37×2.5 mm²) and concentrically copper-screened (...KON, 7×1.5/4KON to 12×2.5/2.5KON) mining control cables

## Quality and supply
(N)SHÖU 0.6/1 kV Flexible Mining & Industrial Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test — 3.0–3.5 kV AC (50 Hz, 5 min) on main cores · 2.0 kV AC on control cores | Every manufactured length (DIN VDE 0250-812 / DIN VDE 0472-508)
Routine test | Conductor DC resistance & construction check — Class 5 copper resistance per DIN VDE 0295 / IEC 60228 (DIN VDE 0472-501) | Every manufactured length
Type test | Oil immersion & vertical flame propagation — Oil resistance per IEC 60811-404 (VDE 0472-803) & flame retardance per IEC 60332-1-2 (VDE 0472-804) | Type qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)SHÖU-J [or -O / ...KON] [size] 0.6/1 kV DIN VDE 0250-812 · [year] · [metre mark]
Supply | Delivery form: Standard 500 m / 1000 m export wooden drums or custom cut lengths (yellow or black 5GM5 outer sheath)
Supply | Submersible pump option: Approved for submersible pump supply down to 500 m depth at water temperatures up to +40 °C (EN 50525-2-21)
Supply | Customs HS code: 8544.49