## Request a quote
Request a quotation for (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812)
Share governing standard (IEC/NEK/BS/IEEE/JIS/VG), voltage rating, core count × cross-section, armour/sheath type (SHF1/SHF2/SW4/Type P) and total length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-shou-j-n-shou-o-0-6-1-kv-vde-0250-812/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
(N)SHÖU-J & (N)SHÖU-O 0.6/1 kV VDE 0250-812 Shore-to-Ship & Deck Rubbe – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shou-j-n-shou-o-0-6-1-kv-vde-0250-812/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-812 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| (N)SHOU-J 3×16+1G16 mm² | 3 × 16 + 1G16 mm² (4G16) | IEC 60228 Class 2/5 Cu/SnCu | 22.4 | 920 | 3.8 | 135 | (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) Construction Schedule (−40…+90 °C)
| (N)SHOU-J 3×35+1G16 mm² | 3 × 35 + 1G16 mm² (4G35) | IEC 60228 Class 2/5 Cu/SnCu | 28.8 | 1690 | 7.4 | 175 | (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) Construction Schedule (−40…+90 °C)
| (N)SHOU-J 3×70+1G35 mm² | 3 × 70 + 1G35 mm² (4G70) | IEC 60228 Class 2/5 Cu/SnCu | 38.2 | 3260 | 14.8 | 230 | (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) Construction Schedule (−40…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0250-812 / IEC 60228 Class 5.

## Electrical, optical & thermal p
(N)SHÖU-J & (N)SHÖU-O 0.6/1 kV VDE 0250-812 Shore-to-Ship & Deck Rubbe – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shou-j-n-shou-o-0-6-1-kv-vde-0250-812/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-812 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 16 + 1G16 mm² (4G16) | 1.15 | 0.6/1 kV (98 A) | −40…+90 °C
3 × 35 + 1G16 mm² (4G35) | 0.524 | 0.6/1 kV (158 A) | −40…+90 °C
3 × 70 + 1G35 mm² (4G70) | 0.268 | 0.6/1 kV (245 A) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
(N)SHÖU-J & (N)SHÖU-O 0.6/1 kV VDE 0250-812 Shore-to-Ship & Deck Rubbe – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shou-j-n-shou-o-0-6-1-kv-vde-0250-812/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-812 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per DIN VDE 0250-812)
Key data | Operating temp. | −40…+90 °C (Continuous shipboard & offshore service)
Key data | Min. bend radius | 6 × OD (Marine tray, bulkhead & deck routing)
Key data | Core / conductor | Class 5 Flexible (DIN VDE 0295 Class 5 finely stranded cop)
Key data | Outer protection | 5GM3 / 5GM5 Heav (High-visibility yellow oil-, seawater- a)
Key data | Standard | DIN VDE 0250-812 (DIN VDE 0250-812 / IEC 60228 Class 5)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (DIN VDE 0250-812 / IEC 60228 Class 5)
Electrical | Core / conductor construction | Class 5 Flexible Copper (5G25 mm²) — DIN VDE 0295 Class 5 finely stranded copper conductors
Electrical | Primary dielectric / buffering | 3GI3 90 °C EPR Core Insulation — VDE 0207 Teil 20 3GI3 ethylene-propylene rubber insulation
Thermal | Continuous operating temperature | −40…+90 °C (shipboard & offshore duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0250-812 / IEC 60228 Class 5
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | 5GM3 / 5GM5 Heavy Polychloroprene Jacket — High-visibility yellow oil-, seawater- and tear-resistant rubber sheath
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Armour, screen & mechanical duty | GM1b Elastomeric Inner Sheath — Pressure-tight extruded EPR inner bedding sheath (up to 500 m water depth)
Resistance | Flame, fire & smoke performance | Qualified for marine flame-retardance and low-smoke zero-halogen / fire safety per DIN VDE 0250-812 / IEC 60228 Class 5
Resistance | Oil, drilling mud & seawater resistance | Resistant to marine fuel/lube oils, salt mist and offshore fluids per DIN VDE 0250-812 / IEC 60228 Class 5
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0250-812 / IEC 60228 Class 5
Standards | Environmental & test standards | IEC 60228 / IEC 60332-3-22 / IEC 60754 / IEC 61034 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812)
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (5GM3 / 5GM5 Heav)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
(N)SHÖU-J & (N)SHÖU-O 0.6/1 kV VDE 0250-812 Shore-to-Ship & Deck Rubbe – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shou-j-n-shou-o-0-6-1-kv-vde-0250-812/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-812 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Flexible Copper (5G25 mm²) | DIN VDE 0295 Class 5 finely stranded copper conductors
2 | 3GI3 90 °C EPR Core Insulation | VDE 0207 Teil 20 3GI3 ethylene-propylene rubber insulation
3 | GM1b Elastomeric Inner Sheath | Pressure-tight extruded EPR inner bedding sheath (up to 500 m water depth)
4 | 5GM3 / 5GM5 Heavy Polychloroprene Jacket | High-visibility yellow oil-, seawater- and tear-resistant rubber sheath
| (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) — Standard Shipboard & Offshore Execution | Built to DIN VDE 0250-812 / IEC 60228 Class 5 with class 5 flexible copper (5g25 mm²) and 5gm3 / 5gm5 heavy polychloroprene jacket
| (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) — Custom Drum Length & Gland Kit | Available in custom continuous shipboard/offshore drum lengths or with marine EMC cable glands
| (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) — Class & Routine Test Certified | Supplied with EN 10204 3.1 routine dielectric, conductor resistance & flame/fire test report

## Quality and supply
(N)SHÖU-J & (N)SHÖU-O 0.6/1 kV VDE 0250-812 Shore-to-Ship & Deck Rubbe – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-shou-j-n-shou-o-0-6-1-kv-vde-0250-812/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-812 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0250-812 / IEC 60228 Class 5) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0250-812 / IEC 60228 Class 5 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0250-812 / IEC 60228 Class 5) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Flame, fire integrity, oil/mud & mechanical qualification (DIN VDE 0250-812 / IEC 60228 Class 5) — Verified flame/fire performance, fluid resistance and thermal stability across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | DIN VDE 0250-812 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)SHOU-J & (N)SHOU-O 0.6/1 KV (VDE 0250-812) DIN VDE 0250-812 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel marine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shipboard/offshore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP