## Request a quote
Request a quotation for (N)SSHCÖU VFD
Application engineer · VFD & mining drive cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/vfd-mining-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)SSHCÖU 0.6/1 kV VFD Mining Cable – Dimensions & electrical data (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812 · (N)SSHCÖU. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation · cores × mm² | Cond. Ø max mm | OD min mm | OD max mm | Mass ≈ kg/km | Max. tensile N | DC resist. 20 °C Ω/km | Capacitance µF/km | Inductance mH/km | Current (30 °C) A | Short-circuit 1 s kA
| (N)SSHCÖU · 3 × 16 + 3 × 2.5 mm² | 5.4 | 24.4 | 27.4 | 1190 | 720 | 1.24 | 0.42 | 0.26 | 99 | 2.29
| (N)SSHCÖU · 3 × 25 + 3 × 4 mm² | 6.3 | 28.2 | 31.2 | 1680 | 1125 | 0.795 | 0.42 | 0.26 | 131 | 3.58
| (N)SSHCÖU · 3 × 35 + 3 × 16/3 mm² | 7.5 | 30.5 | 33.5 | 2000 | 1575 | 0.565 | 0.49 | 0.25 | 162 | 5.01
| (N)SSHCÖU · 3 × 50 + 3 × 25/3 mm² | 8.9 | 36 | 39 | 2820 | 2250 | 0.393 | 0.51 | 0.25 | 202 | 7.15
| (N)SSHCÖU · 3 × 70 + 3 × 35/3 mm² | 10.6 | 41.2 | 44.2 | 3800 | 3150 | 0.277 | 0.59 | 0.24 | 250 | 10.01
| (N)SSHCÖU · 3 × 95 + 3 × 50/3 mm² | 12.1 | 45.7 | 48.7 | 4760 | 4275 | 0.21 | 0.6 | 0.24 | 301 | 13.59
| (N)SSHCÖU · 3 × 120 + 3 × 70/3 mm² | 14.1 | 48.7 | 52.7 | 5890 | 5400 | 0.164 | 0.69 | 0.23 | 352 | 17.16
| (N)SSHCÖU · 3 × 150 + 3 × 70/3 mm² | 16 | 55.7 | 59.7 | 7230 | 6750 | 0.132 | 0.7 | 0.23 | 404 | 21.45
| (N)SSHCÖU · 3 × 185 + 3 × 95/3 mm² | 17.8 | 60.4 | 64.4 | 8640 | 8325 | 0.108 | 0.71 | 0.23 | 461 | 26.46
| (N)SSHCÖU · 3 × 240 + 3 × 120/3 mm² | 20.2 | 68.2 | 72.2 | 11100 | 10800 | 0.0817 | 0.73 | 0.23 | 540 | 34.32
In '3 × 16 + 3 × 2.5' and '3 × 25 + 3 × 4', 2.5 mm² and 4 mm² denote the cross-section of each of the 3 split earth conductors; from 35 mm² upward, '3 × 16/3' denotes 3 split earth conductors with a combined cross-section of 16 mm² (5.33 mm² each).
Current capacity values are nominal for rubber cables laid on a surface at 30 °C ambient per DIN VDE 0298-4 Table 15.

## Technical data
(N)SSHCÖU 0.6/1 kV VFD Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812 · (N)SSHCÖU. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Also permitted 640/1,140 V AC)
Key data | Core arrangement | 3P + 3PE + EMC (Symmetrical 3+3 + Cu braid)
Key data | Size range | 16–240 mm² (10 sizes · 99 to 540 A)
Key data | Max. tensile load | 15 N/mm² (720 to 10,800 N by size)
Key data | Torsional stress | ±25 °/m (Semi-flexible & trailing)
Key data | Temp. (flexing) | −25 to +90 °C (−40 °C fixed (−45 °C option))
Electrical | Rated voltage U0/U | 0.6/1 kV (also permitted for U0/U = 640/1,140 V systems)
Electrical | Max. operating voltage | AC: 0.7/1.2 kV · DC: 0.9/1.8 kV
Electrical | AC test voltage | 5.0 kV, 5 min (main cores)
Electrical | EMC screen & earth symmetry | Symmetrical 3 + 3 split PE in outer interstices + overall concentric tinned copper wire braid
Electrical | Current rating basis | 99 to 540 A (laid on surface at 30 °C ambient per DIN VDE 0298-4 Table 15)
Thermal | Ambient temperature, flexing | −25 °C to +90 °C (standard); −45 °C to +90 °C (low-temp black variant)
Thermal | Ambient temperature, fixed | −40 °C to +90 °C (−45 °C on low-temp variant)
Thermal | Max. conductor temperature | +90 °C continuous · +250 °C short-circuit
Mechanical | Max. tensile load | 15 N/mm² of total power-conductor cross-section (720 to 10,800 N)
Mechanical | Torsional stress | ±25 °/m
Mechanical | Min. bending radius | Per DIN VDE 0298-3 (5 × OD fixed; 10 × OD flexible guiding)
Resistance | Flame retardance | IEC 60332-1-2 vertical flame; MSHA flame resistance
Resistance | Oil resistance | IEC 60811-404 (5GM5 polychloroprene elastomer outer sheath)
Resistance | Water submersion | Submersible in water up to +40 °C to approx. 10 m depth
Resistance | Weather & ozone | UV, ozone and moisture resistant for indoor, underground and opencast service
Standards | Construction standard | Based on DIN VDE 0250-812 · (N)SSHCÖU
Standards | Conductor standard | DIN EN 60228 / IEC 60228 Class 5 (finely stranded tinned copper)
Standards | Compounds | Insulation: 3GI3 EPR · Inner sheath: GM1b EPR · Outer sheath: 5GM5 CR (DIN VDE 0207)
Identification | Core identification | Natural-coloured EPR insulation with printed black numbers; 3 split green-yellow/bare PE cores
Identification | Outer sheath colour | Yellow (standard 5GM5) or Black (−45 °C low-temperature variant)
Identification | Designation | (N)SSHCÖU 0.6/1 kV (EMC-screened heavy rubber motor cable)

## Construction
(N)SSHCÖU 0.6/1 kV VFD Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812 · (N)SSHCÖU. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase & PE conductors | Finely stranded tinned annealed copper, Class 5 | DIN EN 60228 / IEC 60228
2 | Core insulation | Ozone- and heat-resistant EPR elastomer, compound type 3GI3 (natural with black numbers) | DIN VDE 0207-20
3 | Symmetrical PE cores (3) | Three split protective-earth conductors laid symmetrically in the three outer interstices | 120° symmetrical return path
4 | Inner sheath | Vulcanised EPR rubber compound, type GM1b, filling core interstices | DIN VDE 0207-21
5 | EMC concentric screen | EMC-optimised concentric braid of tinned copper wires over inner sheath
6 | Outer sheath | Heavy-duty synthetic chloroprene elastomer (CR), compound type 5GM5, yellow (or black −45 °C) | DIN VDE 0207-21
| (N)SSHCÖU · Yellow 5GM5 | Standard −40 °C fixed / −25 °C flexible construction with high-visibility yellow 5GM5 outer sheath for opencast, underground & tunnelling
| (N)SSHCÖU (−45 °C) · Black 5GM5 | Cold-climate opencast variant rated down to −45 °C with black 5GM5 chloroprene outer sheath

## Quality and supply
(N)SSHCÖU 0.6/1 kV VFD Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812 · (N)SSHCÖU. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage test on main cores — 5.0 kV AC for 5 minutes | Every drum length
Routine test | Conductor & EMC screen DC resistance + spark test — 20 °C DC resistance per DIN EN 60228 Class 5 and 100 % in-line spark test | Every drum length
Sample test | Flame & oil resistance verification — IEC 60332-1-2 vertical flame, MSHA flame, and IEC 60811-404 oil immersion | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · (N)SSHCÖU 0.6/1 kV · [3 × phase + 3 × PE] · VDE 0250-812 · [year] · [metre mark]
Supply | Delivery form: Export seaworthy fumigated wooden drums
Supply | Lengths: Custom cut-to-length reels per VFD motor feeder schedule
Supply | Certificate: EN 10204 3.1 inspection certificate per drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None