## Request a quote
Request a quotation for (N)TMCGC11Y
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-tmcgc11y-single-core-mv-pur-sheathed-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)TMCGC11Y Single-Core MV PUR-Sheathed Cable – 6/10 kV & 12/20 kV dimensions & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tmcgc11y-single-core-mv-pur-sheathed-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | VDE designation | Conductor / Cu screen | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Air 30°C A | Series
| (N)TMCGC11Y 1×50/16 6/10kV | 50 mm² Cl.5 + 16 mm² Cu screen | 24.2 | 920 | 0.393 | 238 | 6/10 kV (N)TMCGC11Y
| (N)TMCGC11Y 1×95/16 6/10kV | 95 mm² Cl.5 + 16 mm² Cu screen | 28 | 1410 | 0.206 | 358 | 6/10 kV (N)TMCGC11Y
| (N)TMCGC11Y 1×185/25 6/10kV | 185 mm² Cl.5 + 25 mm² Cu screen | 33.8 | 2410 | 0.108 | 540 | 6/10 kV (N)TMCGC11Y
| (N)TMCGC11Y 1×50/16 12/20kV | 50 mm² Cl.5 + 16 mm² Cu screen | 28.6 | 1150 | 0.393 | 242 | 12/20 kV (N)TMCGC11Y
| (N)TMCGC11Y 1×120/16 12/20kV | 120 mm² Cl.5 + 16 mm² Cu screen | 33.8 | 1910 | 0.164 | 418 | 12/20 kV (N)TMCGC11Y
| (N)TMCGC11Y 1×240/25 12/20kV | 240 mm² Cl.5 + 25 mm² Cu screen | 40.5 | 3280 | 0.0817 | 645 | 12/20 kV (N)TMCGC11Y
Also manufactured in 3.6/6 kV, 8.7/15 kV and 18/30 kV voltage classes from 25 mm² up to 630 mm².

## Technical data
(N)TMCGC11Y Single-Core MV PUR-Sheathed Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tmcgc11y-single-core-mv-pur-sheathed-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | DIN VDE 0250-813 (Based on flexible MV rubber std)
Key data | Voltage classes | 3.6/6 to 18/30 k (6/10, 8.7/15, 12/20, 18/30 kV)
Key data | Cross-sections | 1 × 25 to 630 mm (Class 5 tinned Cu (IEC 60228))
Key data | Field control + In | G + 3GI3 EPR + G (Triple-extruded +90 °C EPR)
Key data | Earth screen | C (10–35 mm² Cu) (Concentric tinned Cu wire/braid)
Key data | Outer sheath | 11YM1 PUR (Red) (Abrasion, oil & UV resistant)
Electrical | Rated voltage tiers (Uo/U) | 3.6/6 kV · 6/10 kV · 8.7/15 kV · 12/20 kV · 18/30 kV (Umax up to 36 kV)
Electrical | Routine AC test voltage | 11 kV (3.6/6) · 17 kV (6/10) · 29 kV (12/20) · 43 kV (18/30) for 5 min
Electrical | Partial discharge level | ≤ 5 pC at 1.73 × Uo
Electrical | Max. DC resistance @ 20 °C | 0.393 Ω/km (50) · 0.206 Ω/km (95) · 0.129 Ω/km (150) · 0.0817 Ω/km (240)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C (up to 5 s)
Thermal | Ambient temperature range | -40 °C to +80 °C (fixed) · -25 °C to +80 °C (flexible handling)
Mechanical | Min. bend radius | 5 × OD (fixed routing) · 10 × OD (flexible / mobile movement)
Mechanical | Max. tensile load | 15 N / mm² of copper power conductor cross-section
Mechanical | Sheath tear & abrasion | 11YM1 PUR tear strength ≥ 20 N/mm; abrasion < 100 mm³
Resistance | Oil, grease & hydrolysis | 11YM1 polyether PUR resists ASTM #2 oil, hydraulic fluids & microbes
Resistance | Halogen-free outer sheath | 11YM1 polyurethane is naturally halogen-free
Resistance | Weather, UV & water | Ozone proof and suitable for outdoor / wet industrial installation
Standards | Design standard | Based on DIN VDE 0250-813 & DIN VDE 0207-20 / 0207-21
Standards | Installation & ampacity | DIN VDE 0298-3 & DIN VDE 0298-4
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | VDE code breakdown | (N)TM=Flexible MV · C=Screen · G=EPR+Semicon · C=Screen · 11Y=PUR sheath
Identification | Standard sheath colour | Red (RAL 3000), Yellow or Black
Identification | Customs tariff (HS) | 8544.6010

## Construction
(N)TMCGC11Y Single-Core MV PUR-Sheathed Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tmcgc11y-single-core-mv-pur-sheathed-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 fine-stranded tinned copper conductor | Electrolytic tin-coated annealed flexible copper wires per IEC 60228 / DIN VDE 0295 Class 5 (25 mm² to 630 mm²)
2 | Inner semiconducting elastomer stress-control layer ('G') | Vulcanized semiconducting rubber co-extruded over the conductor
3 | 3GI3 Ethylene Propylene Rubber (EPR) MV dielectric | Ozone- and corona-resistant 90 °C thermoset EPR compound Type 3GI3 per DIN VDE 0207-20
4 | Outer semiconducting rubber ('G') + Tinned Cu screen ('C') | Easy-strip outer semiconducting elastomer + concentric helical tinned copper wire / counter-helix or braid screen ('C', 10–35 mm²)
5 | 11YM1 Polyurethane ('11Y') heavy-duty outer sheath | Ether-based thermoplastic polyurethane compound Type 11YM1 per DIN VDE 0207-21 (Red RAL 3000, Yellow or Black)
| (N)TMCGC11Y 6/10 kV (1×25/10 to 1×500/35 mm²) | 6/10 kV (Umax 12 kV) screened flexible single-core EPR/PUR cable for industrial 10/11 kV switchgear and motors
| (N)TMCGC11Y 12/20 kV (1×35/16 to 1×500/35 mm²) | 12/20 kV (Umax 24 kV) screened flexible single-core EPR/PUR cable for 20/22 kV substation transformers and mobile skids
| (N)TMCGC11Y 18/30 kV (1×50/16 to 1×630/35 mm²) | 18/30 kV (Umax 36 kV) screened flexible single-core EPR/PUR cable for 30/33/35 kV wind, mining and grid jumpers

## Quality and supply
(N)TMCGC11Y Single-Core MV PUR-Sheathed Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tmcgc11y-single-core-mv-pur-sheathed-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % High-voltage AC dielectric (11–43 kV) & partial discharge (< 5 pC) test — Zero breakdown for 5 min and PD ≤ 5 pC at 1.73 × Uo | Every manufactured drum length
Type test | 3GI3 EPR ozone, hot-set & bending-plus-thermal-cycle test — PD remains ≤ 5 pC after 3 bending cycles and +95 °C heating cycles | Type qualification
Sample test | 11YM1 polyurethane tear strength, abrasion & hot-oil immersion — Meets DIN VDE 0207-21 mechanical and oil retention limits | Per production batch
Standard / approval | DIN VDE 0250-813 Compliant
Standard / approval | IEC 60502-2 PD Tested
Standard / approval | RoHS 2, REACH & CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)TMCGC11Y 12/20kV VDE 0250-813 CE
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP