## Request a quote
Request a quotation for (N)TSCGECEWÖU MT PLUS
Share immersion depth (AD8), pump motor kW/voltage, water medium (potable/sewage/thermal) and required cut lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-tscgecewoeu-mt-plus/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
(N)TSCGECEWÖU MT PLUS 3.6/6–12/20 kV Submersible MV Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgecewoeu-mt-plus/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-813 / WRAS / ACS. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| (N)TSCGECEWÖU MT P 4G16 mm² | 4G16 mm² (3×16 + 1G16) | IEC 60228 Class 5 flexible Cu/SnCu | 21.8 | 840 | 2.4 | 130 | (N)TSCGECEWÖU MT PLUS Construction Schedule (−25…+90 °C)
| (N)TSCGECEWÖU MT P 4G35 mm² | 4G35 mm² (3×35 + 1G16) | IEC 60228 Class 5 flexible Cu/SnCu | 28.6 | 1620 | 5.2 | 172 | (N)TSCGECEWÖU MT PLUS Construction Schedule (−25…+90 °C)
| (N)TSCGECEWÖU MT P 3×70 + 3G16 mm² | 3 × 70 mm² + 3G16 mm² | IEC 60228 Class 5 flexible Cu/SnCu | 38.4 | 3180 | 10.5 | 230 | (N)TSCGECEWÖU MT PLUS Construction Schedule (−25…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0250-813 / WRAS / ACS.

## Electrical, optical & thermal p
(N)TSCGECEWÖU MT PLUS 3.6/6–12/20 kV Submersible MV Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgecewoeu-mt-plus/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-813 / WRAS / ACS. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
4G16 mm² (3×16 + 1G16) | 1.21 | 3.6/6 kV (94 A submerged) | −25…+90 °C
4G35 mm² (3×35 + 1G16) | 0.554 | 3.6/6 kV (152 A submerged) | −25…+90 °C
3 × 70 mm² + 3G16 mm² | 0.272 | 3.6/6 kV (235 A submerged) | −25…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
(N)TSCGECEWÖU MT PLUS 3.6/6–12/20 kV Submersible MV Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgecewoeu-mt-plus/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-813 / WRAS / ACS. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 kV (Tested per VDE 0250-813)
Key data | Operating temp. | −25…+90 °C (Continuous subsea & marine service)
Key data | Min. bend radius | 10 × OD (Dynamic sheave & fixed routing)
Key data | Core / conductor | 3×25–120 mm² (Class 5 SnCu + indiv. Cu braid screens)
Key data | Outer protection | 5GM3 CM/Blue EM6 (300 m subm. 5GM3 black or WRAS/ACS blue)
Key data | Standard | VDE 0250-813 (DIN VDE 0250-813 / WRAS / ACS)
Electrical | Rated voltage / transmission duty | 3.6/6 kV (DIN VDE 0250-813 / WRAS / ACS)
Electrical | Core / conductor construction | Class 5 Tinned Copper MV Conductors — Flexible stranded tinned copper conductors rated for 3.6/6 kV up to 12/20 kV
Electrical | Primary dielectric / buffering | Triple-Extruded 3GI3 EPR MV Insulation — Semiconductive conductor screen + 3GI3 EPR dielectric + outer semiconductive screen
Thermal | Continuous operating temperature | −25…+90 °C (subsea, marine & submersible duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0250-813 / WRAS / ACS
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | 5GM3 CM / Blue EM6 Potable-Water Sheath — Black 5GM3 CM (MV Submersible) or Blue WRAS/ACS EM6 (MT PLUS, 300 m)
Mechanical | Minimum bending radius | 10 × OD
Mechanical | Hydrostatic, tensile & crush duty | Reinforced Cradle & GM1b Waterproof Inner — Central reinforced rubber cradle + semicon tape + waterproof GM1b EPR inner sheath
Resistance | Hydrostatic pressure & water blocking | Engineered for continuous submersion and hydrostatic integrity per DIN VDE 0250-813 / WRAS / ACS
Resistance | Seawater, oil & chemical resistance | Resistant to seawater hydrolysis, hydraulic oils and abrasion per DIN VDE 0250-813 / WRAS / ACS
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0250-813 / WRAS / ACS
Standards | Environmental & test standards | IEC 60228 / IEC 60332 / ISO 13628-5 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | (N)TSCGECEWÖU MT PLUS
Identification | Sheath colour & metre marking | Continuous metre-marked blue outer finish (5GM3 CM / Blue EM6)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
(N)TSCGECEWÖU MT PLUS 3.6/6–12/20 kV Submersible MV Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgecewoeu-mt-plus/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-813 / WRAS / ACS. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Tinned Copper MV Conductors | Flexible stranded tinned copper conductors rated for 3.6/6 kV up to 12/20 kV
2 | Triple-Extruded 3GI3 EPR MV Insulation | Semiconductive conductor screen + 3GI3 EPR dielectric + outer semiconductive screen
3 | Individual Copper Braid Phase Screen (CE) | Each phase core has its own bare copper braid shield (or 3 split earths in MT PLUS)
4 | Reinforced Cradle & GM1b Waterproof Inner | Central reinforced rubber cradle + semicon tape + waterproof GM1b EPR inner sheath
5 | 5GM3 CM / Blue EM6 Potable-Water Sheath | Black 5GM3 CM (MV Submersible) or Blue WRAS/ACS EM6 (MT PLUS, 300 m)
| (N)TSCGECEWÖU MT PLUS — Standard Subsea & Marine Execution | Built to DIN VDE 0250-813 / WRAS / ACS with class 5 tinned copper mv conductors and 5gm3 cm / blue em6 potable-water sheath
| (N)TSCGECEWÖU MT PLUS — Custom Drum Length & Termination Kit | Available in custom continuous subsea/wellbore drum lengths or pre-terminated assemblies
| (N)TSCGECEWÖU MT PLUS — Routine & Hydrostatic Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & pressure/dimensional report

## Quality and supply
(N)TSCGECEWÖU MT PLUS 3.6/6–12/20 kV Submersible MV Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgecewoeu-mt-plus/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0250-813 / WRAS / ACS. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0250-813 / WRAS / ACS) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0250-813 / WRAS / ACS tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0250-813 / WRAS / ACS) — Zero dielectric breakdown and verified insulation resistance for 3.6/6 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, water-blocking & mechanical endurance qualification (DIN VDE 0250-813 / WRAS / ACS) — Verified submersion integrity, tensile load and thermal stability across −25…+90 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0250-813 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)TSCGECEWÖU MT PLUS VDE 0250-813 3.6/6 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel subsea reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous subsea/wellbore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP