## Request a quote
Request a quotation for (N)TSCGEHXOEU
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/three-core-torsion-resistant-wind-turbine-mv-hv-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)TSCGEHXOEU Three-Core Torsion-Resistant Wind-Turbine MV/HV – 18/30 kV & 20/35 kV dimensions & ratings (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/three-core-torsion-resistant-wind-turbine-mv-hv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2 / IEC 61400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | VDE designation | 3 Phase + 3 Split Earth | Outer Ø ≈ mm | Weight ≈ kg/km | Max. pull kN | Air 30°C A | Series
| (N)TSCGEHXOEU 3×35+3×25/3E 18/30kV | 3 × 35 mm² + 3 × 8.3 mm² E | 58.5 | 4150 | 2.1 | 175 | 18/30 kV (Umax 36 kV) 3-Core Wind Loop
| (N)TSCGEHXOEU 3×50+3×25/3E 18/30kV | 3 × 50 mm² + 3 × 8.3 mm² E | 61.8 | 4780 | 3 | 215 | 18/30 kV (Umax 36 kV) 3-Core Wind Loop
| (N)TSCGEHXOEU 3×70+3×35/3E 18/30kV | 3 × 70 mm² + 3 × 11.7 mm² E | 65.8 | 5690 | 4.2 | 265 | 18/30 kV (Umax 36 kV) 3-Core Wind Loop
| (N)TSCGEHXOEU 3×95+3×50/3E 18/30kV | 3 × 95 mm² + 3 × 16.7 mm² E | 70.2 | 6780 | 5.7 | 320 | 18/30 kV (Umax 36 kV) 3-Core Wind Loop
| (N)TSCGEHXOEU 3×120+3×70/3E 20/35kV | 3 × 120 mm² + 3 × 23.3 mm² E | 76.5 | 8240 | 7.2 | 370 | 20/35 kV (Umax 42 kV) 3-Core Offshore Wind
| (N)TSCGEHXOEU 3×150+3×70/3E 20/35kV | 3 × 150 mm² + 3 × 23.3 mm² E | 80.8 | 9480 | 9 | 415 | 20/35 kV (Umax 42 kV) 3-Core Offshore Wind
Also available in 6/10 kV, 12/20 kV and 38/66 kV (offshore 66 kV array voltage) configurations.

## Technical data
(N)TSCGEHXOEU Three-Core Torsion-Resistant Wind-Turbine MV/HV – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/three-core-torsion-resistant-wind-turbine-mv-hv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2 / IEC 61400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | VDE 0250-813 / I (Wind-turbine MV/HV loop cable)
Key data | Voltage classes | 6/10 to 38/66 kV (12/20, 18/30, 20/35 & 38/66 kV)
Key data | Cross-sections | 3 × 25 to 185 mm (+ 3 split earth cores ('E'))
Key data | Torsion rating | ±100° / m (≥ 10,000 yaw cycles (-40 °C))
Key data | Insulation | 3GI3 EPR (+90 °C (Triple-extruded semicon ('G'))
Key data | Outer sheath | HX-OEU Halogen-F (IEC 60332-3-24 & oil resistant)
Electrical | Rated voltage tiers (Uo/U) | 6/10 kV · 12/20 kV · 18/30 kV · 20/35 kV · 38/66 kV (Umax up to 72.5 kV)
Electrical | Routine AC test & PD | 29 kV (12/20) · 43 kV (18/30) · 50 kV (20/35) · 95 kV (38/66) + PD ≤ 5 pC
Electrical | Max. DC resistance @ 20 °C | 0.393 Ω/km (50) · 0.277 Ω/km (70) · 0.206 Ω/km (95) · 0.132 Ω/km (150)
Electrical | Free-air ampacity (30 °C) | 215 A (3×50) · 265 A (3×70) · 320 A (3×95) · 415 A (3×150)
Thermal | Continuous conductor temp. | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C (up to 5 s)
Thermal | Operating ambient range | -40 °C to +80 °C (qualified for -40 °C cold torsion)
Mechanical | Torsion capability | ±100° / m (up to ±150° / m) over free loop for ≥ 10,000 cycles
Mechanical | Min. bend radius | 6 × OD (fixed tower clamping) · 10 × OD (dynamic nacelle loop)
Mechanical | Max. vertical tensile load | 20 N / mm² of total copper cross-section (self-supporting drop)
Resistance | Tower fire & smoke safety | IEC 60332-3-24 Cat C bunched flame · IEC 60754-1/2 LSZH · IEC 61034-2
Resistance | Hydraulic oil & grease | EN 60811-404 resistant to turbine gearbox & yaw hydraulic oils ('OEU')
Resistance | Offshore salt fog & ozone | ISO 9227 salt-spray, UV and high-voltage ozone resistant
Standards | Design standards | DIN VDE 0250-813 · IEC 60502-2 · IEC 61400 wind turbine series
Standards | Halogen-free standards | IEC 60754-1 / 60754-2 & IEC 61034-2
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | VDE code breakdown | (N)TSCGE=MV/HV torsion 3C+3E · HX=Halogen-free · OEU=Oil/Flame
Identification | Outer sheath colour | Black or Red
Identification | Customs tariff (HS) | 8544.6010

## Construction
(N)TSCGEHXOEU Three-Core Torsion-Resistant Wind-Turbine MV/HV – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/three-core-torsion-resistant-wind-turbine-mv-hv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2 / IEC 61400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 × Torsion-optimized Class 5 / Class 6 tinned copper conductors | Electrolytic tin-coated extra-flexible annealed copper wires with calibrated pitch length for bidirectional twisting (3 × 25 mm² to 3 × 185 mm²)
2 | Triple-extruded inner & outer semiconducting elastomer screens ('G') | Vulcanized inner conductor screen and torsion-stable outer semiconducting elastomer co-extruded with the EPR dielectric
3 | 3GI3 Ethylene Propylene Rubber (EPR) MV/HV dielectric | 90 °C ozone- and corona-resistant thermoset EPR compound Type 3GI3 (6/10 kV up to 20/35 kV & 38/66 kV)
4 | 3 × Split tinned copper interstitial earth cores ('E') | Three semiconducting-sheathed tinned copper earth conductors laid symmetrically in the outer interstices (e.g., 3×25/25E or 3×95/50E)
5 | HX-OEU Halogen-Free, Oil- & Flame-Resistant double sheath | Inner elastomer bedding + open-weave synthetic anti-torsion braid + Black or Red cross-linked halogen-free ('HX') oil-resistant ('OEU') outer sheath
| (N)TSCGEHXOEU 12/20 kV (3×35+3×16/3E to 3×150+3×25E) | 20/22 kV three-core torsion-resistant halogen-free wind-turbine nacelle loop cable for 3–6 MW onshore turbines
| (N)TSCGEHXOEU 18/30 kV & 20/35 kV (3×50+3×25/3E to 3×185+3×35E) | 33/35 kV (Umax 36–42 kV) three-core torsion-resistant MV loop cable for 6–12 MW onshore & offshore wind turbines
| (N)TSCGEHXOEU 38/66 kV (3×70 to 3×185 mm² ·Umax 72.5 kV) | 66 kV high-voltage torsion-resistant nacelle-to-tower loop cable for next-generation 12–18 MW offshore wind turbines

## Quality and supply
(N)TSCGEHXOEU Three-Core Torsion-Resistant Wind-Turbine MV/HV – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/three-core-torsion-resistant-wind-turbine-mv-hv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60502-2 / IEC 61400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % High-voltage AC dielectric (29–95 kV) & PD test (≤ 5 pC @ 1.73 Uo) — Zero breakdown for 5 min and PD ≤ 5 pC on all 3 phase cores | Every manufactured drum
Type test | 10,000-cycle ±100°/m nacelle loop torsion test (-40 °C to +90 °C) + PD check — Zero strand breakage, zero jacket cracking and PD remains ≤ 5 pC after torsion | Wind turbine qualification
Type test | IEC 60332-3-24 vertical tray fire, IEC 60754-2 LSZH & IEC 61034-2 smoke — Passes bunched flame, zero halogen (pH ≥ 4.3) and light transmittance ≥ 60 % | Type qualification
Standard / approval | DIN VDE 0250-813 Compliant
Standard / approval | IEC 60332-3-24 & IEC 60754-2
Standard / approval | Offshore Wind Qualified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)TSCGEHXOEU 3x70+3x35/3E 18/30kV WIND TORSION LSZH VDE 0250-813 CE
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP