## Request a quote
Request a quotation for (N)TSCGEW11Y 6/10 kV Shore Power Cable with FO
Application engineer · Marine HVSC & port reeling cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-tscgew11y-6-10-kv-shore-power-cable-with-fo/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)TSCGEW11Y 6/10 kV HVSC Shore Power Cable with FO – Dimensions & mechanical parameters (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgew11y-6-10-kv-shore-power-cable-with-fo/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/ISO/IEEE 80005-1 · DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation (N)TSCGEW11Y + FO | Phase mm² | Split earth mm² | Screened pilots mm² | Fibre unit IEC 60793-2-10 | Min. OD mm | Max. OD mm | Tensile 25N/mm² N | Mass ≈ kg/km
| 3×70 + 2×35/2 + 1×(8×2.5)C + FO | 70 | 2×35/2 | 8×2.5C | 12×OM1 | 66 | 69 | 5250 | 6505
| 3×95 + 2×50/2 + 1×(8×2.5)C + FO | 95 | 2×50/2 | 8×2.5C | 12×OM1 | 68 | 71 | 7125 | 7440
| 3×120 + 2×70/2 + 1×(8×2.5)C + FO | 120 | 2×70/2 | 8×2.5C | 12×OM1 | 71 | 74 | 9000 | 8465
| 3×185 + 2×95/2 + 1×(8×2.5)C + FO | 185 | 2×95/2 | 8×2.5C | 12×OM1 | 74 | 77 | 13875 | 10000
Max. tensile load is calculated at 25 N/mm² of the three main copper phase conductors (3 × phase mm² × 25 N/mm²).
Minimum bending radius: 6 × D fixed installation, 10 × D free movement, 12 × D reeling operation.

## Technical data
(N)TSCGEW11Y 6/10 kV HVSC Shore Power Cable with FO – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgew11y-6-10-kv-shore-power-cable-with-fo/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/ISO/IEEE 80005-1 · DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6/10 kV (12 kV) (21 kV AC routine test)
Key data | Hybrid core set | 3P+2E+8×2.5C+FO (12 × G62.5/125 OM1 fibres)
Key data | Phase size range | 70–185 mm² (4 HVSC configurations)
Key data | Sheath & water | 11Y TPU · AD8 (Halogen-free · 10 bar water)
Key data | Operating temp. | −30 to +90 °C (Fixed down to −40 °C)
Key data | Max. tensile | 25 N/mm² max (5,250 to 13,875 N pull)
Electrical | Rated & max voltage | U0/U 6/10 kV · Max. operating voltage Umax 6.9/12 kV AC (suitable for 6.6 kV and 11 kV HVSC systems)
Electrical | Routine AC test voltage | 21 kV AC routine dielectric test (elevated above standard 17 kV VDE test for marine HVSC service)
Electrical | Screened pilot bundle | 1 × (8 × 2.5 mm²)C — eight Class 5 tinned copper EPR-insulated cores (white with black numbers) under overall tinned Cu screen
Thermal | Conductor temperature | +90 °C max continuous operation · +200 °C max short-circuit temperature
Thermal | Ambient temperature range | Fixed −40 °C to +90 °C · Mobile and reeling operation −30 °C to +90 °C
Mechanical | Min. bending radius | 6 × D fixed installation · 10 × D free movement · 12 × D motorized reeling
Mechanical | Max. permissible tensile load | 25 N/mm² of main phase copper cross-section (5,250 N on 3×70 mm² up to 13,875 N on 3×185 mm²)
Optical | Fibre count & specification | 12 × G62.5/125 µm (OM1) graded-index multimode fibres to IEC 60793-2-10 (core 62.5 ± 3 µm, cladding 125 ± 2 µm, coating 245 ± 10 µm)
Optical | Attenuation & bandwidth | 850 nm: ≤ 3.2 dB/km & ≥ 200 MHz·km · 1300 nm: ≤ 0.9 dB/km & ≥ 500 MHz·km
Resistance | Submersion & halogen-free TPU | Permanent water immersion up to 10 bar (AD8) · Halogen-free dual TPU (11Y) inner and outer sheaths
Resistance | Marine & dockside durability | Resistant to seawater, marine oils, UV radiation, ozone and concrete quayside abrasion
Standards | Applicable standards | IEC/ISO/IEEE 80005-1 (HVSC) · DIN VDE 0250-813 · DIN VDE 0298-3 · DIN VDE 0298-4
Standards | Conductor & earth construction | 3 Class 5 tinned Cu phase cores (triple-extruded EPR) + 2 split semiconductive-covered tinned Cu ground conductors
Identification | Core & fibre identification | Pilot cores white EPR with black numbers 1–8 · Optical fibres individually colour-coded · Black 11Y TPU outer sheath
Identification | Designation code | (N)TSCGEW11Y — MV reeling cable with triple-extruded EPR cores, anti-torsion braid and 11Y thermoplastic polyurethane sheaths

## Construction
(N)TSCGEW11Y 6/10 kV HVSC Shore Power Cable with FO – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgew11y-6-10-kv-shore-power-cable-with-fo/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/ISO/IEEE 80005-1 · DIN VDE 0250-813. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Main phase conductors | Three Class 5 flexible tinned copper conductors (70, 95, 120 or 185 mm²) | IEC 60228 · DIN VDE 0295
2 | Inner semiconductive layer | Triple-extruded inner semiconductive elastomer stress-control screen | DIN VDE 0250-813
3 | Core insulation | Triple-extruded ethylene-propylene rubber (EPR) dielectric (6/10 kV, 21 kV AC test) | DIN VDE 0207-20
4 | Outer semiconductive layer | Triple-extruded outer semiconductive elastomer layer in contact with split ground conductors | DIN VDE 0250-813
5 | Split ground conductors | Two Class 5 tinned copper ground conductors (2×35/2 to 2×95/2 mm²) with semiconductive covering | IEC/ISO/IEEE 80005-1
6 | Screened pilot bundle 1×(8×2.5)C | Eight 2.5 mm² tinned copper cores (white EPR with black numbers 1–8) under an overall tinned copper wire screen | IEC/ISO/IEEE 80005-1
7 | Optical fibre unit (12 × OM1) | 12 graded-index multimode fibres G62.5/125 µm (IEC 60793-2-10) in protective buffer assembly | IEC 60793-2-10
8 | Inner sheath (11Y) | Halogen-free thermoplastic polyurethane (TPU) inner bedding sheath | DIN VDE 0250-813
9 | Anti-torsion reinforcing braid | High-strength synthetic textile braid vulcanized between inner and outer TPU sheaths
10 | Outer sheath (11Y) | Black halogen-free thermoplastic polyurethane (TPU), AD8 (10 bar) submersible, UV and oil resistant | DIN VDE 0250-813 · AD8
| 3×70 & 3×95 mm² HVSC Umbilicals | 3×70+2×35/2 or 3×95+2×50/2 + 1×(8×2.5)C + 12×OM1 FO · 66–71 mm OD · 6,505–7,440 kg/km
| 3×120 & 3×185 mm² High-Capacity HVSC Umbilicals | 3×120+2×70/2 or 3×185+2×95/2 + 1×(8×2.5)C + 12×OM1 FO · 71–77 mm OD · 8,465–10,000 kg/km

## Quality and supply
(N)TSCGEW11Y 6/10 kV HVSC Shore Power Cable with FO – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tscgew11y-6-10-kv-shore-power-cable-with-fo/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/ISO/IEEE 80005-1 · DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 21 kV AC HVSC dielectric withstand test — 21 kV AC applied to 6/10 kV (Umax 12 kV) triple-extruded EPR phase cores per IEC/ISO/IEEE 80005-1 and datasheet | Every shipping drum
Routine test | OTDR optical attenuation & bandwidth verification — ≤ 3.2 dB/km at 850 nm and ≤ 0.9 dB/km at 1300 nm verified across all 12 G62.5/125 µm OM1 fibres | Every shipping drum
Sample test | AD8 (10 bar) water immersion & halogen-free TPU sheath test — Permanent water submersion up to 10 bar (AD8) plus oil, UV and abrasion testing on dual 11Y TPU sheaths | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · (N)TSCGEW11Y 6/10 kV · IEC 80005-1 · FO
Supply | Delivery form: Export marine wooden or steel reels sized to 12 × D reeling bend radius
Supply | Lengths: Custom shipboard or quayside HVSC dispenser reel lengths
Supply | Certificate: EN 10204 3.1 21 kV AC HV test + 12-fibre OTDR test report with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None