## Request a quote
Request a quotation for (N)TSFLCGEWÖU MV Flat Reeling Cable (3.6/6 & 6/10 kV)
Application engineer · Crane festoon & MV reeling cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-tsflcgewoeu-mv-flat-reeling-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)TSFLCGEWÖU Medium-Voltage Flat Reeling Cable – Dimensions & electrical parameters (3.6/6 & 6/10 kV) (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tsflcgewoeu-mv-flat-reeling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation (N)TSFLCGEWÖU | Voltage kV | Phase mm² | Concentric E mm² | Cond. Ø mm | Min. H mm | Max. H mm | Min. W mm | Max. W mm | Min. bend mm | Mass ≈ kg/km | Max. pull N | DC Res. 20°C Ω/km | Current A | 1s Short-Cct kA
| 3.6/6 kV · 3×25 + 3×25/3E | 3.6/6 | 25 | 3×25/3E | 6.9 | 24.2 | 27.2 | 64.3 | 68.3 | 408 | 2730 | 1125 | 0.8 | 105 | 3.58
| 3.6/6 kV · 3×35 + 3×25/3E | 3.6/6 | 35 | 3×25/3E | 8.3 | 24.7 | 27.7 | 65.8 | 69.8 | 416 | 3120 | 1575 | 0.57 | 130 | 5.01
| 3.6/6 kV · 3×50 + 3×25/3E | 3.6/6 | 50 | 3×25/3E | 9.8 | 27.8 | 30 | 71.1 | 75.1 | 450 | 3860 | 2250 | 0.39 | 162 | 7.15
| 3.6/6 kV · 3×70 + 3×35/3E | 3.6/6 | 70 | 3×35/3E | 11.4 | 28.9 | 31.9 | 76.8 | 80.8 | 479 | 4730 | 3150 | 0.28 | 200 | 10.01
| 3.6/6 kV · 3×95 + 3×50/3E | 3.6/6 | 95 | 3×50/3E | 13.3 | 29.2 | 30.9 | 75.5 | 79.5 | 464 | 5280 | 4275 | 0.21 | 241 | 13.59
| 3.6/6 kV · 3×120 + 3×70/3E | 3.6/6 | 120 | 3×70/3E | 15.1 | 35.4 | 37.4 | 92.3 | 97.3 | 561 | 7400 | 5400 | 0.16 | 282 | 17.16
| 6/10 kV · 3×25 + 3×25/3E | 6/10 | 25 | 3×25/3E | 6.9 | 25 | 27.5 | 66.7 | 69.7 | 413 | 2860 | 1125 | 0.8 | 105 | 3.58
| 6/10 kV · 3×35 + 3×25/3E | 6/10 | 35 | 3×25/3E | 8.3 | 25.5 | 28.5 | 68.2 | 72.2 | 428 | 3260 | 1575 | 0.57 | 130 | 5.01
| 6/10 kV · 4×35 + 4×25/4E | 6/10 | 35 | 4×25/4E | 8.3 | 25.5 | 28.5 | 86.7 | 91.7 | 428 | 4110 | 2100 | 0.57 | 130 | 5.01
| 6/10 kV · 3×50 + 3×25/3E | 6/10 | 50 | 3×25/3E | 9.8 | 28.1 | 31.1 | 74.6 | 78.6 | 467 | 4030 | 2250 | 0.39 | 162 | 7.15
| 6/10 kV · 3×70 + 3×35/3E | 6/10 | 70 | 3×35/3E | 11.4 | 29.7 | 32.7 | 79.2 | 83.2 | 491 | 4850 | 3150 | 0.28 | 200 | 10.01
| 6/10 kV · 4×70 + 4×35/4E | 6/10 | 70 | 4×35/4E | 11.4 | 29.5 | 32.5 | 100.9 | 105.9 | 488 | 6240 | 4200 | 0.28 | 200 | 10.01
| 6/10 kV · 3×95 + 3×50/3E | 6/10 | 95 | 3×50/3E | 13.3 | 31.7 | 34.7 | 84.7 | 89.7 | 521 | 5920 | 4275 | 0.21 | 241 | 13.59
| 6/10 kV · 3×120 + 3×70/3E | 6/10 | 120 | 3×70/3E | 15.1 | 35.1 | 38.1 | 92.9 | 97.9 | 572 | 7420 | 5400 | 0.16 | 282 | 17.16
Per DIN VDE 0298-3, the effective applied diameter for flat cable bending calculations is D = 1.5 × flat cable height (Max. H), yielding the tabulated minimum bending radius of 15 × Max. H (408–572 mm).
On 3.6/6 kV 3×25+3×25/3E, minimum width is corrected to 64.3 mm (datasheet prints 46.3–68.3 mm, a digit transposition of 64.3 mm).

## Technical data
(N)TSFLCGEWÖU Medium-Voltage Flat Reeling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tsflcgewoeu-mv-flat-reeling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 & 6/10 kV (11 kV / 17 kV AC test)
Key data | Core arrangement | 3C or 4C Flat (Parallel cores + 3E/4E screens)
Key data | Phase size range | 25–120 mm² (14 flat configurations)
Key data | Travel speed | Up to 120 m/min (Gantry & festoon service)
Key data | Operating temp. | −35 to +80 °C (Fixed −50 to +80 °C)
Key data | Max. tensile | 15 N/mm² max (1,125 to 5,400 N pull)
Electrical | Rated voltage U0/U | 3.6/6 kV (Um 4.2/7.2 kV AC, 5.4/10.8 kV DC) · 6/10 kV (Um 6.9/12 kV AC, 9/18 kV DC)
Electrical | Routine AC test voltage | 11 kV AC for 3.6/6 kV series · 17 kV AC for 6/10 kV series
Electrical | Current carrying capacity | 105 A (25 mm²) to 282 A (120 mm²) according to DIN VDE 0298-4
Thermal | Conductor temperature | +90 °C max continuous operation · +250 °C max short-circuit (1 s)
Thermal | Ambient temperature range | Fixed −50 °C to +80 °C · Fully flexible −35 °C to +80 °C
Mechanical | Min. bending radius & S-guide | 408 to 572 mm (DIN VDE 0298-3, D_applied = 1.5 × flat cable height) · S-guide distance ≥ 20 × D
Mechanical | Tensile, travel speed & torsion | 15 N/mm² max tensile load (1,125–5,400 N) · Up to 120 m/min gantry reeling speed · Torsion not permitted
Resistance | Sheath & environmental durability | Red polychloroprene (CR / Type 5GM5) outer sheath resistant to oil, ozone, UV, moisture and weather
Resistance | Dynamic bend endurance | Type-tested under reversed bending and high-speed monospiral/festoon reeling cycles
Standards | Construction & application standards | Based on DIN VDE 0250-813 · DIN VDE 0298-3 · DIN VDE 0298-4 · IEC 60228
Standards | Parallel screen geometry | 3 or 4 parallel EPR cores, each with concentrically distributed split copper earth screen (3E or 4E)
Identification | Core & sheath identification | Natural-coloured EPR insulation with black semiconductive layer · Red polychloroprene (CR) outer sheath
Identification | Designation code | (N)TSFLCGEWÖU — Medium-voltage flat ('FL') reeling & festoon cable with concentric per-core earth screens

## Construction
(N)TSFLCGEWÖU Medium-Voltage Flat Reeling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tsflcgewoeu-mv-flat-reeling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductor | Finely stranded tinned electrolytic copper conductor (25 to 120 mm²) | DIN VDE 0295 · IEC 60228
2 | Inner semiconductive layer | Extruded inner semiconductive rubber electrical field control layer | DIN VDE 0250-813
3 | Core insulation | High-grade EPR rubber compound (natural colour) rated 3.6/6 kV or 6/10 kV | DIN VDE 0207-20
4 | Outer semiconductive layer | Extruded black semiconductive rubber outer field control layer | DIN VDE 0250-813
5 | Concentric split earth screen (3E / 4E) | Split tinned copper earth conductor concentrically distributed around each parallel core (25/3E to 70/3E, or 25/4E to 35/4E) | DIN VDE 0250-813
6 | Flat outer sheath | Heavy-duty polychloroprene (CR / Type 5GM5) special elastomer compound, red, oil-, UV-, ozone- and moisture-resistant | DIN VDE 0250-813
| 3.6/6 kV 3-Core Flat Series (25–120 mm²) | 3×25+3×25/3E to 3×120+3×70/3E · 24.2–37.4 mm height × 64.3–97.3 mm width · 11 kV AC test
| 6/10 kV 3-Core & 4-Core Flat Series (25–120 mm²) | 3×25 to 3×120 mm² plus 4-core builds 4×35+4×25/4E and 4×70+4×35/4E (for integrated fibre/control sub-core) · 17 kV AC test

## Quality and supply
(N)TSFLCGEWÖU Medium-Voltage Flat Reeling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tsflcgewoeu-mv-flat-reeling-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 11 kV / 17 kV AC dielectric withstand test — 11 kV AC (3.6/6 kV) or 17 kV AC (6/10 kV) applied to each EPR phase core and concentric earth screen | Every shipping drum
Type test | Reversed bending & high-speed reeling endurance test — Dynamic reversed bending over guide rollers and monospiral/festoon reeling cycles up to 120 m/min | Type qualification
Sample test | −35 °C cold flex & polychloroprene sheath oil/weather test — Verified for −35 °C dynamic flexing, −50 °C fixed cold endurance, oil, ozone and UV resistance | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · (N)TSFLCGEWÖU · VDE 0250-813
Supply | Delivery form: Export wooden reels wound flat without axial twist
Supply | Lengths: Custom crane boom festoon or monospiral reel lengths
Supply | Certificate: EN 10204 3.1 factory routine HV test report with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None