## Request a quote
Request a quotation for N2XH
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n2xh-lszh-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
N2XH LSZH Power Cable – Dimensions, weight & air ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xh-lszh-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-604 / HD 604 S1 / IEC 60502-1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | VDE designation | Cores & stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Air 30°C A | Series
| N2XH-O 1×95 RM | 1 × 95 mm² Class 2 | 17.5 | 980 | 0.193 | 298 | Single-Core N2XH-O
| N2XH-O 1×240 RM | 1 × 240 mm² Class 2 | 25.8 | 2380 | 0.0754 | 538 | Single-Core N2XH-O
| N2XH-J 5×2.5 RE | 5G2.5 mm² Class 1 | 12.2 | 225 | 7.41 | 29 | Five-Core N2XH-J (3P+N+PE)
| N2XH-J 5×16 RM | 5G16 mm² Class 2 | 21.4 | 985 | 1.15 | 94 | Five-Core N2XH-J (3P+N+PE)
| N2XH-J 5×50 RM | 5G50 mm² Class 2 | 33.5 | 2680 | 0.387 | 183 | Five-Core N2XH-J (3P+N+PE)
| N2XH-J 5×95 RM | 5G95 mm² Class 2 | 44.2 | 4950 | 0.193 | 282 | Five-Core N2XH-J (3P+N+PE)
For installations requiring functional circuit integrity (FE180 / E30–E90) during a fire, specify NHXH E30/E90.

## Technical data
N2XH LSZH Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xh-lszh-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-604 / HD 604 S1 / IEC 60502-1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | VDE 0276-604 (HD 604 S1 / IEC 60502-1)
Key data | Voltage rating | 0.6/1 kV (4,000 V AC test voltage)
Key data | Configurations | 1C to 5C (-J/-O) (1.5 to 500 mm² Cu Cl. 1/2)
Key data | Insul. / Sheath | 2XI1 XLPE / HM4 (+90 °C XLPE + LSZH jacket)
Key data | CPR fire class | Cca-s1,d1,a1 (B2ca option for escape routes)
Key data | Temperature | -30 to +90 °C (+250 °C short-circuit rating)
Electrical | Rated voltage (Uo/U) | 0.6 / 1 kV AC (max. 1.2 kV AC / 1.8 kV DC)
Electrical | AC routine test voltage | 4,000 V AC rms for 5 minutes
Electrical | Max. DC resistance @ 20 °C | 1.15 Ω/km (16) · 0.387 Ω/km (50) · 0.193 Ω/km (95) · 0.0754 Ω/km (240)
Electrical | Volume resistivity @ 90 °C | ≥ 10¹² Ω·cm (2XI1 XLPE dielectric)
Thermal | Continuous conductor temp. | +90 °C (vs +70 °C for PVC NYY)
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Thermal | Ambient temperature range | -30 °C to +70 °C (fixed) · -5 °C to +50 °C (laying)
Mechanical | Min. bend radius | 15 × OD (single-core N2XH-O) · 12 × OD (multi-core N2XH-J)
Mechanical | Max. pulling tension | 50 N / mm² of total copper conductor cross-section
Mechanical | Impact & abrasion | High-density HM4 polyolefin sheath resists tray pulling damage
Resistance | Bunched flame propagation | IEC 60332-3-24 Cat C & EN 50575 CPR Cca-s1,d1,a1 (B2ca opt)
Resistance | Corrosive gas & acidity | IEC 60754-1/2: pH ≥ 4.3, conductivity ≤ 2.5 µS/mm
Resistance | Smoke density | IEC 61034-2: light transmittance ≥ 60 %
Standards | Design standards | DIN VDE 0276-604 · HD 604 S1 · IEC 60502-1
Standards | Core colour standard | HD 308 S2 / DIN VDE 0293-308
Standards | RoHS, REACH & CE | EU CPR 305/2011 DoP, 2011/65/EU RoHS 2 & REACH
Identification | VDE code breakdown | N=VDE std · 2X=XLPE · H=Halogen-free HM4 · -J=with GNYE · -O=without GNYE
Identification | Core colours (5-core -J) | Green/Yellow, Blue, Brown, Black, Grey (HD 308 S2)
Identification | Customs tariff (HS) | 8544.4993

## Construction
N2XH LSZH Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xh-lszh-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-604 / HD 604 S1 / IEC 60502-1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Bare annealed copper conductor (RE / RM / SM) | Solid Class 1 ('RE', 1.5–16 mm²) or stranded Class 2 ('RM' circular / 'SM' sector, 16–500 mm²) bare copper per IEC 60228
2 | 2XI1 Cross-Linked Polyethylene (XLPE) insulation | 90 °C thermoset XLPE compound Type 2XI1 per HD 604 S1, colour-coded per HD 308 S2
3 | Halogen-free flame-retardant inner filling compound | Unvulcanized mineral-filled halogen-free elastomeric inner bedding filling core interstices
4 | HM4 Low-Smoke Zero-Halogen (LSZH) outer sheath | Thermoplastic halogen-free polyolefin compound Type HM4 (Black, UV-stabilized)
| N2XH-O (1 × 16 to 1 × 500 mm² Single-Core) | Single-core 0.6/1 kV XLPE/LSZH feeder cable without green/yellow core for parallel trefoil bus feeders
| N2XH-J (3G1.5 to 5G240 mm² Multi-Core) | 3-, 4- and 5-core 0.6/1 kV XLPE/LSZH distribution cable with green/yellow protective earth core ('-J')

## Quality and supply
N2XH LSZH Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xh-lszh-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0276-604 / HD 604 S1 / IEC 60502-1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 4.0 kV AC dielectric, spark & DC resistance test — Zero breakdown for 5 min and DC R within IEC 60228 limits | Every manufactured drum length
Type test | EN 50399 / IEC 60332-3-24 vertical tray fire & heat release test — Meets CPR Euroclass Cca-s1,d1,a1 (or B2ca-s1,d1,a1) | Notified Body CPR certification
Sample test | IEC 60754-2 acid gas pH/conductivity & IEC 61034-2 smoke density — pH ≥ 4.3, conductivity ≤ 2.5 µS/mm, light transmittance ≥ 60 % | Per production batch
Standard / approval | DIN VDE 0276-604 & HD 604 S1
Standard / approval | EN 50575 CPR Cca / B2ca
Standard / approval | IEC 60502-1 & RoHS 2
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX N2XH-J / N2XH-O 0.6/1kV VDE 0276-604 Cca-s1,d1,a1 CE
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP