## Request a quote
Request a quotation for N2XSEYFGbY
Application engineer · armoured mining power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n2xseyfgby-6-10kv-xlpe-copper-screened-flat-steel-wire-armoured-feeder-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
N2XSEYFGbY 6/10 kV XLPE Flat-Steel-Armoured Feeder Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xseyfgby-6-10kv-xlpe-copper-screened-flat-steel-wire-armoured-feeder-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| N2XSEYFGbY 3×70/16 mm² 6/10 kV | 3 × 70 mm² / 16 mm² SE | Class 2 compacted Cu | 54 | 4560 | 31.5 | 810 | N2XSEYFGbY Construction Schedule (-20 to +90 °C)
| N2XSEYFGbY 3×95/16 mm² 6/10 kV | 3 × 95 mm² / 16 mm² SE | Class 2 compacted Cu | 58.2 | 5480 | 42.8 | 875 | N2XSEYFGbY Construction Schedule (-20 to +90 °C)
| N2XSEYFGbY 3×150/25 mm² 6/10 kV | 3 × 150 mm² / 25 mm² SE | Class 2 compacted Cu | 65.5 | 7490 | 67.5 | 985 | N2XSEYFGbY Construction Schedule (-20 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0276-620 / IEC 60502-2.

## Electrical, optical & thermal p
N2XSEYFGbY 6/10 kV XLPE Flat-Steel-Armoured Feeder Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xseyfgby-6-10kv-xlpe-copper-screened-flat-steel-wire-armoured-feeder-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 70 mm² / 16 mm² SE | 0.268 | 6/10 kV (250 A in ground) | -20 to +90 °C
3 × 95 mm² / 16 mm² SE | 0.193 | 6/10 kV (298 A in ground) | -20 to +90 °C
3 × 150 mm² / 25 mm² SE | 0.124 | 6/10 kV (385 A in ground) | -20 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
N2XSEYFGbY 6/10 kV XLPE Flat-Steel-Armoured Feeder Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xseyfgby-6-10kv-xlpe-copper-screened-flat-steel-wire-armoured-feeder-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6/10 kV (6/10 kV (U_m = 12 kV) MV distribution)
Key data | Operating temp. | -20 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 15 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×50–240 mm² Cu (Class 2 compacted copper + Cu screen)
Key data | Outer protection | FGb + FR-PVC (Flat steel wire + counter-tape + PVC)
Key data | Standard | VDE 0276-620 (DIN VDE 0276-620 / IEC 60502-2)
Electrical | Rated voltage / transmission duty | 6/10 kV (DIN VDE 0276-620 / IEC 60502-2)
Electrical | Core / conductor construction | Phase Conductors (3×95 mm²) — IEC 60228 Class 2 compacted circular plain copper conductors
Electrical | Primary dielectric / buffering | Triple-Extruded XLPE Core (2X) — Inner semicon + 90 °C dry-cured XLPE dielectric + strippable outer semicon
Thermal | Continuous operating temperature | -20 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0276-620 / IEC 60502-2
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Outer Sheath (FR-PVC) — Heavy-duty flame-retardant, oil- and UV-resistant PVC outer jacket
Mechanical | Minimum bending radius | 15 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per DIN VDE 0276-620 / IEC 60502-2
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per DIN VDE 0276-620 / IEC 60502-2
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per DIN VDE 0276-620 / IEC 60502-2
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0276-620 / IEC 60502-2
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | N2XSEYFGbY
Identification | Sheath colour & metre marking | Continuous metre-marked red mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
N2XSEYFGbY 6/10 kV XLPE Flat-Steel-Armoured Feeder Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xseyfgby-6-10kv-xlpe-copper-screened-flat-steel-wire-armoured-feeder-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase Conductors (3×95 mm²) | IEC 60228 Class 2 compacted circular plain copper conductors
2 | Triple-Extruded XLPE Core (2X) | Inner semicon + 90 °C dry-cured XLPE dielectric + strippable outer semicon
3 | Individual Copper Wire Screen (SE) | Helically applied plain copper wires with counter-helix copper tape
4 | PVC Bedding & Steel Armour (FGb) | PVC inner sheath + galvanized flat steel wires (F) + steel counter tape (Gb)
5 | Outer Sheath (FR-PVC) | Heavy-duty flame-retardant, oil- and UV-resistant PVC outer jacket
| N2XSEYFGbY — Standard Mining Execution | Built to DIN VDE 0276-620 / IEC 60502-2 with phase conductors (3×95 mm²) and outer sheath (fr-pvc)
| N2XSEYFGbY — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| N2XSEYFGbY — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
N2XSEYFGbY 6/10 kV XLPE Flat-Steel-Armoured Feeder Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n2xseyfgby-6-10kv-xlpe-copper-screened-flat-steel-wire-armoured-feeder-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0276-620 / IEC 60502-2) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0276-620 / IEC 60502-2 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0276-620 / IEC 60502-2) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (DIN VDE 0276-620 / IEC 60502-2) — Verified flame retardancy, mechanical integrity and thermal endurance across -20 to +90 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0276-620 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX N2XSEYFGbY VDE 0276-620 6/10 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP