## Request a quote
Request a quotation for NC
Application engineer · furnace & process pyrometry
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-n-thermocouple-compensating-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NC Type N Thermocouple Compensating Cable – Dimensions, construction & weights (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-n-thermocouple-compensating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / BS EN 50288-7. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Insulation / Sheath | Junction range | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| NCB-PVC-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | PVC / PVC (OS) | 0…+100 °C | 5.6 | 44 | 42 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-PiMF 2×2×0.5 | 2×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | 0…+100 °C | 8.6 | 84 | 64 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | 0…+100 °C | 10.8 | 142 | 81 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-PiMF 8×2×0.5 | 8×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | 0…+100 °C | 14.1 | 246 | 106 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-PiMF 12×2×0.5 | 12×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | 0…+100 °C | 16.9 | 348 | 127 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | PVC / PVC (OS) | 0…+100 °C | 6.7 | 68 | 50 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-PiMF 4×2×1.0 | 4×2×1.0 mm² (7/0.43) | PVC / PVC (PiMF+OS) | 0…+100 °C | 12.8 | 212 | 96 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-OS 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | PVC / PVC (OS) | 0…+100 °C | 7.5 | 92 | 56 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCB-PVC-PiMF 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | PVC / PVC (PiMF+OS) | 0…+100 °C | 14.3 | 286 | 107 | NCB PVC / PVC Screened Marshalling Cables (0…+100 °C)
| NCA-FEP-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | FEP / FEP (OS) | 0…+200 °C | 5.6 | 58 | 42 | NCA FEP / FEP Extended-Range Compensating Cables (0…+200 °C)
| NCA-FEP-PiMF 4×2×1.0 | 4×2×1.0 mm² (7/0.43) | FEP / FEP (PiMF+OS) | 0…+200 °C | 11.2 | 188 | 84 | NCA FEP / FEP Extended-Range Compensating Cables (0…+200 °C)
| NCB-XLPE-SWA 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | 0…+90 °C | 12.1 | 298 | 121 | NCB XLPE / LSZH / SWA Armoured Direct-Burial Trunks (0…+90 °C)
| NCB-XLPE-SWA 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | 0…+90 °C | 19.8 | 745 | 198 | NCB XLPE / LSZH / SWA Armoured Direct-Burial Trunks (0…+90 °C)
| NCB-XLPE-SWA 8×2×1.5 | 8×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | 0…+90 °C | 25.4 | 1210 | 254 | NCB XLPE / LSZH / SWA Armoured Direct-Burial Trunks (0…+90 °C)
Do not interchange KCB and NCB: although both use Cu/CuNi alloys, NCB uses a different CuNi composition matched to ~27.7 µV/°C instead of ~40.6 µV/°C.

## NC vs NX loop resistance & tole
NC Type N Thermocouple Compensating Cable – NC vs NX loop resistance & tolerance comparison (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-n-thermocouple-compensating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / BS EN 50288-7. Values for your order are confirmed in the quotation.
IEC 60584-3 code | Conductor alloys (+ / −) | Junction temp. range | Tolerance | Loop R @ 1.0 mm² Ω/m ≈
NX (True Extension) | (+) NiCrSi / (−) NiSi | −25 °C to +200 °C | Class 1: ±1.5 °C (±39 µV) | 1.35
NCA (Compensating) | (+) Cu / (−) CuNi (N-cal) | 0 °C to +200 °C | Class 2: ±2.5 °C (±65 µV) | 0.36
NCB (Compensating) | (+) Cu / (−) CuNi (N-cal) | 0 °C to +100 °C | Class 2: ±2.5 °C (±65 µV) | 0.36
NC cuts loop resistance from 1.35 Ω/m to 0.36 Ω/m at 1.0 mm², preventing high source impedance faults on long DCS input runs.

## Technical data
NC Type N Thermocouple Compensating Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-n-thermocouple-compensating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / BS EN 50288-7. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Compensates for | Type N (NiCrSi) (Nicrosil-Nisil thermocouples)
Key data | Alloy pair | Cu (+) / CuNi (Copper (+) / N-calibrated CuNi (−))
Key data | Junction ranges | 0…+100 / +200 °C (NCB (0…+100 °C) · NCA (0…+200 °C))
Key data | EMF tolerance | Class 2: ±2.5 °C (±65 µV (measured at 900 °C))
Key data | Loop resistance | ≈ 0.36 Ω/m/pair (at 1.0 mm² (vs 1.35 Ω/m on NX))
Key data | IEC colour code | + Pink / − White (Pink outer jacket (or Ex-i Blue))
Electrical | Compensated thermocouple type | Type N (Nicrosil-Nisil, NiCrSi-NiSi) per IEC 60584-1
Electrical | Positive conductor (+) | High-conductivity Copper (Cu, non-magnetic, ~1.72 µΩ·cm)
Electrical | Negative conductor (−) | Type-N-calibrated Copper-Nickel (CuNi alloy, non-magnetic, ~34 µΩ·cm)
Electrical | Tolerance Class 2 (IEC 60584-3) | ±2.5 °C (±65 µV) over 0…+100 °C (NCB) or 0…+200 °C (NCA)
Electrical | Loop resistance @ 20 °C | ≈ 0.72 Ω/m (0.5 mm²) · 0.36 Ω/m (1.0 mm²) · 0.24 Ω/m (1.5 mm²)
Thermal | Permissible junction temperature range | 0 °C to +100 °C (Type NCB) · 0 °C to +200 °C (Type NCA)
Thermal | Insulation rating (by jacket type) | −25…+105 °C (PVC) · −40…+90 °C (XLPE/LSZH) · −60…+200 °C (FEP)
Mechanical | Conductor stranding | 0.5 mm² (7/0.30) · 1.0 mm² (7/0.43) · 1.5 mm² (7/0.53)
Mechanical | Min. bending radius | 7.5 × OD (unarmoured) · 10 × OD (SWA armoured)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat C
Resistance | Corrosion resistance | 100 % non-ferrous Cu/CuNi conductors
Standards | Thermocouple cable standard | IEC 60584-3 & ANSI/ISA MC96.1
Standards | Cable construction standard | BS EN 50288-7 / BS 5308
Identification | IEC 60584-3 colour code | (+) Pink · (−) White · Outer sheath: Pink (or Blue Ex-i)
Identification | ANSI MC96.1 colour code | (+) Orange · (−) Red · Outer sheath: Orange
Identification | Customs tariff (HS) | 8544.49

## Construction
NC Type N Thermocouple Compensating Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-n-thermocouple-compensating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / BS EN 50288-7. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Matched Type NC (NCA/NCB) compensating conductors | Positive (+): High-purity Copper (Cu) · Negative (−): Type-N-calibrated Copper-Nickel (CuNi ~70/30 alloy), 7-wire stranded
2 | Colour-coded core insulation | Flame-retardant PVC, XLPE or +200 °C FEP (IEC: + Pink / − White; ANSI: + Orange / − Red)
3 | Individual & collective Al/PET screens | Aluminium/PET laminated tape + 0.5 mm² tinned copper drain wire (OS or PiMF+OS) | 100 % electrostatic shielding
4 | Optional SWA armour | Unarmoured or Galvanised Steel Wire Armour (SWA) over extruded bedding
5 | Outer jacket (Pink RAL 3015, Orange or Ex-i Blue) | Flame-retardant PVC, Low-Smoke Zero-Halogen (LSZH), or fluoropolymer FEP | IEC 60332-1-2 / IEC 60332-3-24 flame retardant
| NCB — IEC 60584-3 (0…+100 °C) | Positive (+) Pink, Negative (−) White, Outer Jacket Pink (RAL 3015) for ambient marshalling boxes
| NCA — Extended Range (0…+200 °C) | FEP/HR-PVC insulated NCA compensating alloy pair calibrated up to +200 °C
| NCB-XLPE-SWA (Armoured Trunk) | XLPE insulated, SWA armoured multi-pair trunk cable

## Quality and supply
NC Type N Thermocouple Compensating Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-n-thermocouple-compensating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / BS EN 50288-7. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Thermoelectric EMF calibration test (IEC 60584-3 Class 2) — EMF deviation within ±2.5 °C (±65 µV) over 0…+100 °C (NCB) or 0…+200 °C (NCA) | Every alloy batch
Routine test | 1500 V / 2000 V AC dielectric & continuity test — 1 min AC withstand test without breakdown | Every manufactured drum
Standard / approval | IEC 60584-3 Class 2 (NCA / NCB) Certified
Standard / approval | BS EN 50288-7 & BS 5308 Compliant
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NC TYPE N COMPENSATING <size> IEC 60584-3 CLASS 2 CE
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP