## Request a quote
Request a quotation for NEK 606 BFOU / RFOU
Include the NEK 606 code (e.g. RFOU P1/P8, BFOU P5/P12, RFOU(i) S1/S5 or BFOU(i) S3/S7), core/pair count and mm² size, sheath colour (Black, Red, Grey or Ex-i Blue) and classification society requirements.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NEK 606 BFOU & RFOU Mud-Resistant Offshore Cables – Dimensions & mass (83) (83)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NEK TS 606 / IEC 60092-353, -354, -376 & -360 (SHF2). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores / Pairs × mm² | Voltage grade | NEK 606 code | Insulation wall (mm) | Bedding OD (mm) | SHF2 wall (mm) | Nominal OD (mm) | Copper mass (kg/km) | Total mass (kg/km) | Series
| RFOU 0.6/1 kV 1×16/2.5 mm² | 1 × 16/2.5 mm² | 0.6/1 kV | P1 / P8 | 1 | 9.5 | 1.1 | 12.5 | 196 | 330 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×35/6 mm² | 1 × 35/6 mm² | 0.6/1 kV | P1 / P8 | 1.2 | 12.5 | 1.3 | 16.5 | 405 | 620 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×70/6 mm² | 1 × 70/6 mm² | 0.6/1 kV | P1 / P8 | 1.4 | 16 | 1.4 | 20 | 735 | 1060 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×95/10 mm² | 1 × 95/10 mm² | 0.6/1 kV | P1 / P8 | 1.6 | 18 | 1.5 | 22.5 | 985 | 1380 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×150/10 mm² | 1 × 150/10 mm² | 0.6/1 kV | P1 / P8 | 1.8 | 22 | 1.6 | 26.5 | 1510 | 2020 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×240/16 mm² | 1 × 240/16 mm² | 0.6/1 kV | P1 / P8 | 2.2 | 27.5 | 1.8 | 32.5 | 2371 | 3090 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×300/16 mm² | 1 × 300/16 mm² | 0.6/1 kV | P1 / P8 | 2.4 | 30.5 | 1.9 | 35.5 | 2975 | 3810 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 1×500/25 mm² | 1 × 500/25 mm² | 0.6/1 kV | P1 / P8 | 2.4 | 37.5 | 2.2 | 44 | 4894 | 6180 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 2×1.5/4 mm² | 2 × 1.5/4 mm² | 0.6/1 kV | P1 / P8 | 1 | 9.5 | 1.1 | 12.5 | 80 | 260 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×1.5/4 mm² | 3 × 1.5/4 mm² | 0.6/1 kV | P1 / P8 | 1 | 10 | 1.2 | 13.5 | 95 | 310 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 7×1.5/6 mm² | 7 × 1.5/6 mm² | 0.6/1 kV | P1 / P8 | 1 | 13 | 1.3 | 17 | 197 | 500 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 12×1.5/10 mm² | 12 × 1.5/10 mm² | 0.6/1 kV | P1 / P8 | 1 | 17.5 | 1.5 | 21.5 | 300 | 740 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 19×1.5/10 mm² | 19 × 1.5/10 mm² | 0.6/1 kV | P1 / P8 | 1 | 20.5 | 1.6 | 25 | 413 | 1020 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 37×1.5/16 mm² | 37 × 1.5/16 mm² | 0.6/1 kV | P1 / P8 | 1 | 27.5 | 1.9 | 32.5 | 713 | 1720 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×2.5/6 mm² | 3 × 2.5/6 mm² | 0.6/1 kV | P1 / P8 | 1 | 11 | 1.3 | 14.5 | 152 | 390 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×6/6 mm² | 3 × 6/6 mm² | 0.6/1 kV | P1 / P8 | 1 | 13.5 | 1.4 | 17.5 | 263 | 590 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×16/16 mm² | 3 × 16/16 mm² | 0.6/1 kV | P1 / P8 | 1 | 18 | 1.5 | 22 | 621 | 1110 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×35/16 mm² | 3 × 35/16 mm² | 0.6/1 kV | P1 / P8 | 1.2 | 24.5 | 1.7 | 29 | 1126 | 1920 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×70/35 mm² | 3 × 70/35 mm² | 0.6/1 kV | P1 / P8 | 1.4 | 33 | 2 | 39 | 2346 | 3690 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×120/60 mm² | 3 × 120/60 mm² | 0.6/1 kV | P1 / P8 | 1.6 | 41 | 2.3 | 48 | 3953 | 5930 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×185/95 mm² | 3 × 185/95 mm² | 0.6/1 kV | P1 / P8 | 2 | 50.5 | 2.7 | 59.5 | 6278 | 9220 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| RFOU 0.6/1 kV 3×240/120 mm² | 3 × 240/120 mm² | 0.6/1 kV | P1 / P8 | 2.2 | 57.5 | 3 | 67.5 | 8063 | 11820 | RFOU 0.6/1 kV (P1/P8) — Flame-Retardant Power & Control
| BFOU 0.6/1 kV 1×16/4 mm² | 1 × 16/4 mm² | 0.6/1 kV | P5 / P12 | 1 | 10 | 1.2 | 13 | 196 | 370 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 1×50/6 mm² | 1 × 50/6 mm² | 0.6/1 kV | P5 / P12 | 1.4 | 15 | 1.4 | 18.5 | 546 | 860 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 1×95/10 mm² | 1 × 95/10 mm² | 0.6/1 kV | P5 / P12 | 1.6 | 18.5 | 1.5 | 23 | 985 | 1420 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 1×150/10 mm² | 1 × 150/10 mm² | 0.6/1 kV | P5 / P12 | 1.8 | 23 | 1.7 | 27.5 | 1510 | 2100 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 1×240/16 mm² | 1 × 240/16 mm² | 0.6/1 kV | P5 / P12 | 2.2 | 28 | 1.8 | 33 | 2371 | 3170 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 1×300/16 mm² | 1 × 300/16 mm² | 0.6/1 kV | P5 / P12 | 2.4 | 31 | 1.9 | 36 | 2975 | 3890 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 2×1.5/4 mm² | 2 × 1.5/4 mm² | 0.6/1 kV | P5 / P12 | 1 | 10 | 1.2 | 13 | 80 | 285 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×1.5/6 mm² | 3 × 1.5/6 mm² | 0.6/1 kV | P5 / P12 | 1 | 10.5 | 1.3 | 14.5 | 125 | 360 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 7×1.5/6 mm² | 7 × 1.5/6 mm² | 0.6/1 kV | P5 / P12 | 1 | 14 | 1.4 | 18 | 214 | 560 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 12×1.5/10 mm² | 12 × 1.5/10 mm² | 0.6/1 kV | P5 / P12 | 1 | 18.5 | 1.6 | 23 | 316 | 830 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 19×1.5/10 mm² | 19 × 1.5/10 mm² | 0.6/1 kV | P5 / P12 | 1 | 22 | 1.7 | 26.5 | 438 | 1130 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 37×1.5/16 mm² | 37 × 1.5/16 mm² | 0.6/1 kV | P5 / P12 | 1 | 30 | 2 | 35.5 | 738 | 1950 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×2.5/6 mm² | 3 × 2.5/6 mm² | 0.6/1 kV | P5 / P12 | 1 | 11.5 | 1.3 | 15 | 168 | 420 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×6/6 mm² | 3 × 6/6 mm² | 0.6/1 kV | P5 / P12 | 1 | 14 | 1.4 | 18 | 280 | 620 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×10/10 mm² | 3 × 10/10 mm² | 0.6/1 kV | P5 / P12 | 1 | 16 | 1.5 | 20 | 389 | 800 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×16/16 mm² | 3 × 16/16 mm² | 0.6/1 kV | P5 / P12 | 1 | 19 | 1.6 | 23.5 | 621 | 1190 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×35/16 mm² | 3 × 35/16 mm² | 0.6/1 kV | P5 / P12 | 1.2 | 25.5 | 1.8 | 30.5 | 1126 | 2040 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| BFOU 0.6/1 kV 3×70/35 mm² | 3 × 70/35 mm² | 0.6/1 kV | P5 / P12 | 1.4 | 34 | 2.1 | 40 | 2346 | 3810 | BFOU 0.6/1 kV (P5/P12) — Fire-Resistant Power & Control
| RFOU(i) 250 V 1P 0.75 mm² | 1 Pair × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 6.5 | 1 | 9.5 | 52 | 160 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 2P 0.75 mm² | 2 Pairs × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 9.5 | 1.1 | 12.5 | 104 | 280 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 4P 0.75 mm² | 4 Pairs × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 11 | 1.2 | 15 | 181 | 410 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 8P 0.75 mm² | 8 Pairs × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 14.5 | 1.4 | 18.5 | 283 | 640 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 12P 0.75 mm² | 12 Pairs × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 17.5 | 1.5 | 22 | 376 | 860 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 16P 0.75 mm² | 16 Pairs × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 19.5 | 1.6 | 24 | 469 | 1050 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 24P 0.75 mm² | 24 Pairs × 0.75 mm² | 150/250 V | S1 / S5 | 0.6 | 24.5 | 1.9 | 29.5 | 646 | 1510 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 1P 1.5 mm² | 1 Pair × 1.5 mm² | 150/250 V | S1 / S5 | 0.7 | 7.5 | 1.1 | 10.5 | 79 | 210 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 2P 1.5 mm² | 2 Pairs × 1.5 mm² | 150/250 V | S1 / S5 | 0.7 | 11.5 | 1.3 | 15.5 | 175 | 410 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 4P 1.5 mm² | 4 Pairs × 1.5 mm² | 150/250 V | S1 / S5 | 0.7 | 13.5 | 1.4 | 17.5 | 258 | 550 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 8P 1.5 mm² | 8 Pairs × 1.5 mm² | 150/250 V | S1 / S5 | 0.7 | 18 | 1.6 | 22.5 | 428 | 910 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(i) 250 V 16P 1.5 mm² | 16 Pairs × 1.5 mm² | 150/250 V | S1 / S5 | 0.7 | 24.5 | 1.9 | 29.5 | 749 | 1580 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(c) 250 V 4P 0.75 mm² | 4 Pairs × 0.75 mm² | 150/250 V | S2 / S6 | 0.6 | 10.5 | 1.2 | 14.5 | 150 | 360 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| RFOU(c) 250 V 8P 1.5 mm² | 8 Pairs × 1.5 mm² | 150/250 V | S2 / S6 | 0.7 | 17.5 | 1.5 | 22 | 382 | 820 | RFOU(i) & RFOU(c) 250 V (S1–S6) — Instrumentation
| BFOU(i) 250 V 1P 0.75 mm² | 1 Pair × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 7.5 | 1 | 10.5 | 56 | 195 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 2P 0.75 mm² | 2 Pairs × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 11 | 1.3 | 14.5 | 137 | 360 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 4P 0.75 mm² | 4 Pairs × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 12.5 | 1.4 | 16.5 | 190 | 500 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 8P 0.75 mm² | 8 Pairs × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 17 | 1.6 | 21.5 | 296 | 810 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 12P 0.75 mm² | 12 Pairs × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 20.5 | 1.7 | 25 | 394 | 1070 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 16P 0.75 mm² | 16 Pairs × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 23 | 1.8 | 27.5 | 492 | 1330 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 24P 0.75 mm² | 24 Pairs × 0.75 mm² | 150/250 V | S3 / S7 | 0.6 | 29 | 2.1 | 34.5 | 749 | 2020 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 1P 1.5 mm² | 1 Pair × 1.5 mm² | 150/250 V | S3 / S7 | 0.7 | 9 | 1.1 | 12 | 79 | 255 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 2P 1.5 mm² | 2 Pairs × 1.5 mm² | 150/250 V | S3 / S7 | 0.7 | 13 | 1.4 | 17 | 185 | 480 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 4P 1.5 mm² | 4 Pairs × 1.5 mm² | 150/250 V | S3 / S7 | 0.7 | 15.5 | 1.5 | 19.5 | 270 | 670 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 8P 1.5 mm² | 8 Pairs × 1.5 mm² | 150/250 V | S3 / S7 | 0.7 | 21 | 1.7 | 25.5 | 449 | 1120 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(i) 250 V 16P 1.5 mm² | 16 Pairs × 1.5 mm² | 150/250 V | S3 / S7 | 0.7 | 29 | 2 | 34 | 773 | 1970 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(c) 250 V 4P 0.75 mm² | 4 Pairs × 0.75 mm² | 150/250 V | S4 / S8 | 0.6 | 12.5 | 1.4 | 16 | 160 | 450 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| BFOU(c) 250 V 8P 1.5 mm² | 8 Pairs × 1.5 mm² | 150/250 V | S4 / S8 | 0.7 | 20.5 | 1.7 | 25 | 403 | 1020 | BFOU(i) & BFOU(c) 250 V (S3–S8) — Fire-Resistant Instrumentation
| RFOU 3.6/6 kV 3×25/16 mm² | 3 × 25/16 mm² | 3.6/6 (7.2) kV | P2 / P102 | 2.5 | 34.5 | 2.2 | 41.2 | 1180 | 2900 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 3.6/6 kV 3×50/25 mm² | 3 × 50/25 mm² | 3.6/6 (7.2) kV | P2 / P102 | 2.5 | 41 | 2.4 | 47.6 | 1960 | 4100 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 3.6/6 kV 3×95/50 mm² | 3 × 95/50 mm² | 3.6/6 (7.2) kV | P2 / P102 | 2.5 | 49.5 | 2.7 | 56.9 | 3610 | 6250 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 3.6/6 kV 3×150/70 mm² | 3 × 150/70 mm² | 3.6/6 (7.2) kV | P2 / P102 | 2.5 | 57 | 3 | 65.4 | 5390 | 8600 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 3.6/6 kV 3×240/50 mm² | 3 × 240/50 mm² | 3.6/6 (7.2) kV | P2 / P102 | 2.6 | 65.5 | 3.3 | 74.2 | 8150 | 12200 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 1×35/11 mm² | 1 × 35/11 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 21 | 1.7 | 26 | 611 | 1200 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 1×70/16 mm² | 1 × 70/16 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 23.5 | 1.9 | 30 | 971 | 1700 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 1×120/20 mm² | 1 × 120/20 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 27.5 | 2 | 34 | 1506 | 2350 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 1×185/18 mm² | 1 × 185/18 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 30.5 | 2.1 | 36.5 | 2138 | 3100 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 1×240/21 mm² | 1 × 240/21 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 33 | 2.1 | 39 | 2702 | 3800 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 3×25/31 mm² | 3 × 25/31 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 42 | 2.4 | 49.5 | 1465 | 3800 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 3×50/31 mm² | 3 × 50/31 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 47 | 2.8 | 55 | 2124 | 5000 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 3×95/50 mm² | 3 × 95/50 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 54 | 2.8 | 62.5 | 3975 | 7500 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 3×150/75 mm² | 3 × 150/75 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 60 | 3.2 | 70.5 | 5634 | 9800 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
| RFOU 6/10 kV 3×240/53 mm² | 3 × 240/53 mm² | 6/10 (12) kV | P3 / P10 | 3.4 | 69.5 | 3.5 | 79.5 | 8609 | 13300 | RFOU 3.6/6 kV & 6/10(12) kV (P2/P3/P102) — Medium-Voltage Power
In power cable designations (e.g. 3 × 95/50 mm²), the number after the slash indicates the equivalent cross-section (mm²) of the tinned copper wire braid (TCWB) armour/earth screen.
Bedding OD (diameter over inner covering 'F') and Nominal OD (diameter over outer SHF2 sheath 'U') are nominal values for selecting Ex d / Ex e double-compression offshore cable glands.

## Electrical & short-circuit
NEK 606 BFOU & RFOU Mud-Resistant Offshore Cables – Electrical & short-circuit (21) (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NEK TS 606 / IEC 60092-353, -354, -376 & -360 (SHF2). Values for your order are confirmed in the quotation.
Designation | Cores × mm² | Max. R_DC at 20 °C (Ω/km) | Max. R_AC at 90 °C (Ω/km) | Reactance 50 Hz (Ω/km) | Reactance 60 Hz (Ω/km) | Current rating 45 °C (A) | 1 s short-circuit (A)
RFOU / BFOU 1×16 mm² | 1 × 16 mm² | 1.16 | 1.48 | 0.116 | 0.14 | 96 | 2240
RFOU / BFOU 1×35 mm² | 1 × 35 mm² | 0.529 | 0.675 | 0.106 | 0.128 | 157 | 4900
RFOU / BFOU 1×70 mm² | 1 × 70 mm² | 0.27 | 0.344 | 0.099 | 0.119 | 242 | 9800
RFOU / BFOU 1×95 mm² | 1 × 95 mm² | 0.195 | 0.249 | 0.097 | 0.116 | 293 | 13300
RFOU / BFOU 1×150 mm² | 1 × 150 mm² | 0.126 | 0.161 | 0.092 | 0.111 | 389 | 21000
RFOU / BFOU 1×240 mm² | 1 × 240 mm² | 0.076 | 0.097 | 0.089 | 0.107 | 522 | 33600
RFOU / BFOU 1×300 mm² | 1 × 300 mm² | 0.061 | 0.077 | 0.087 | 0.105 | 601 | 42000
RFOU / BFOU 3×1.5 mm² | 3 × 1.5 mm² | 12.2 | 15.6 | 0.11 | 0.132 | 16 | 210
RFOU / BFOU 3×2.5 mm² | 3 × 2.5 mm² | 7.56 | 9.64 | 0.103 | 0.123 | 21 | 350
RFOU / BFOU 3×6 mm² | 3 × 6 mm² | 3.11 | 3.97 | 0.09 | 0.108 | 36 | 840
RFOU / BFOU 3×10 mm² | 3 × 10 mm² | 1.84 | 2.35 | 0.084 | 0.101 | 50 | 1400
RFOU / BFOU 3×16 mm² | 3 × 16 mm² | 1.16 | 1.48 | 0.08 | 0.096 | 67 | 2240
RFOU / BFOU 3×25 mm² | 3 × 25 mm² | 0.734 | 0.936 | 0.079 | 0.095 | 89 | 3500
RFOU / BFOU 3×35 mm² | 3 × 35 mm² | 0.529 | 0.675 | 0.076 | 0.092 | 110 | 4900
RFOU / BFOU 3×50 mm² | 3 × 50 mm² | 0.391 | 0.499 | 0.076 | 0.092 | 137 | 7000
RFOU / BFOU 3×70 mm² | 3 × 70 mm² | 0.27 | 0.344 | 0.074 | 0.088 | 169 | 9800
RFOU / BFOU 3×95 mm² | 3 × 95 mm² | 0.195 | 0.249 | 0.073 | 0.088 | 205 | 13300
RFOU / BFOU 3×120 mm² | 3 × 120 mm² | 0.154 | 0.196 | 0.072 | 0.086 | 237 | 16800
RFOU / BFOU 3×150 mm² | 3 × 150 mm² | 0.126 | 0.161 | 0.072 | 0.087 | 272 | 21000
RFOU / BFOU 3×185 mm² | 3 × 185 mm² | 0.1 | 0.128 | 0.072 | 0.086 | 311 | 25900
RFOU / BFOU 3×240 mm² | 3 × 240 mm² | 0.076 | 0.097 | 0.072 | 0.086 | 365 | 33600
Continuous current ratings are based on IEC 60092-352 Table B.4 at 45 °C ambient air temperature and 90 °C maximum conductor temperature. For other ambient temperatures apply rating factors: 35 °C (1.10), 40 °C (1.05), 50 °C (0.94), 55 °C (0.88).
Instrumentation pairs/triples electrical values: 0.75 mm² (R_20 ≤ 24.8 Ω/km, L ≈ 0.67 mH/km, C ≈ 110 nF/km, L/R ≤ 14.3 µH/Ω); 1.5 mm² (R_20 ≤ 12.2 Ω/km, L ≈ 0.63 mH/km, C ≈ 125 nF/km, L/R ≤ 26.6 µH/Ω); 2.5 mm² (R_20 ≤ 7.56 Ω/km, L ≈ 0.59 mH/km, C ≈ 145 nF/km, L/R ≤ 39.0 µH/Ω).

## Technical data
NEK 606 BFOU & RFOU Mud-Resistant Offshore Cables – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NEK TS 606 / IEC 60092-353, -354, -376 & -360 (SHF2). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage | 250 V – 12/20 kV (250 V inst. · 0.6/1 kV LV · 3.6–20 kV MV)
Key data | Conductor temp. | +90 °C (Continuous · +250 °C short-circuit)
Key data | Fire integrity | IEC 60331-21 (BFOU: 750 °C for 90–180 min)
Key data | Outer sheath | SHF2 Mud (IEC 60092-360 SHF2 · NEK 606 mud)
Key data | Min. bend radius | 6 × D / 8 × D (LV/inst. 6 × D fixed · MV 9 × D fixed)
Key data | Armour / screen | TCWB ('O') (Tinned copper wire braid (≥ 90 %))
Electrical | Instrumentation voltage | 150/250 V (S1/S5, S2/S6, S3/S7, S4/S8)
Electrical | LV power & control voltage | 0.6/1 kV (RFOU P1/P8 & BFOU P5/P12)
Electrical | MV power voltage grades | 3.6/6(7.2) kV, 6/10(12) kV & 12/20(24) kV
Electrical | Instrumentation capacitance | 110–145 nF/km (shielded); 100–125 nF/km (unshielded)
Thermal | Max. conductor temperature | +90 °C continuous
Thermal | Short-circuit temperature | +250 °C (5 s maximum)
Thermal | Fixed operating range | −40 °C to +90 °C (fixed); −20 °C min. install
Mechanical | Conductor stranding | Tinned stranded circular copper, IEC 60228 Class 2 (or 5)
Mechanical | Min. bend radius (LV & inst.) | 6 × D fixed installed; 8 × D during pulling
Mechanical | Min. bend radius (MV power) | 9 × D fixed installed; 15 × D during pulling
Mechanical | Max. pulling tensile load | 50 N/mm² of total copper cross-section
Resistance | Fire resistance (BFOU series) | IEC 60331-21 / IEC 60331-11 (750 °C, 90–180 min)
Resistance | Flame retardance (all series) | IEC 60332-1-2 & IEC 60332-3-22 Category A
Resistance | Halogen-free & low smoke | IEC 60754-1/2 (< 0.5 % HCl) & IEC 61034-1/2 (≥ 60 %)
Resistance | Drilling mud resistance | NEK TS 606 SHF2 mud (IRM 902/903, CaBr2 & ester fluids)
Standards | Offshore & marine design | NEK TS 606; IEC 60092-353 / -354 / -376
Standards | Materials & conductors | IEC 60228; IEC 60092-351 (EPR); IEC 60092-360 (SHF2)
Identification | Outer sheath colour code | Black (LV power); Red (MV power); Grey or Blue (Ex-i inst.)
Identification | Core identification | HD 308 S2 colours (≤ 5C), numbered (> 5C), pairs Bk/Bu

## Construction
NEK 606 BFOU & RFOU Mud-Resistant Offshore Cables – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NEK TS 606 / IEC 60092-353, -354, -376 & -360 (SHF2). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper conductor | Tinned annealed stranded circular copper (STCC) per IEC 60228 Class 2 (Class 5 flexible available on request) | IEC 60228
2 | Mica glass fire-barrier tape ('B' — BFOU series only) | Helically lapped phlogopite/muscovite mica glass tape maintaining dielectric circuit integrity at 750 °C–830 °C per IEC 60331-21 | IEC 60331-21
3 | Halogen-free EPR insulation ('R' / 'B') | High-grade ethylene propylene rubber (EPR) per IEC 60092-351, rated +90 °C continuous and +250 °C short-circuit | IEC 60092-351
4 | Individual / collective foil screen ('(i)' / '(c)' inst. series) | Copper-backed polyester tape with tinned copper drain wire over each pair/triple ('(i)') or over the collective bundle ('(c)') | IEC 60092-376
5 | Halogen-free inner covering ('F') | Extruded flame-retardant, halogen-free bedding compound filling core interstices to form a gas-tight circular profile for Ex glands | NEK TS 606
6 | Tinned copper wire braid armour ('O') | Tinned annealed copper wire braid (TCWB) serving as combined mechanical armour and concentric earth/EMC screen | IEC 60092-353 / NEK TS 606
7 | Thermoset SHF2 mud-resistant outer sheath ('U') | Cross-linked halogen-free, low-smoke, flame-retardant elastomer compound (SHF2 per IEC 60092-360) meeting NEK TS 606 mud resistance | IEC 60092-360 / NEK TS 606
| RFOU 0.6/1 kV (P1/P8) & RFOU(i)/(c) 250 V (S1/S5, S2/S6) | Flame-retardant (IEC 60332-3-22 Cat. A), halogen-free, mud-resistant power, control and instrumentation cables with EPR insulation, TCWB armour and SHF2 sheath.
| BFOU 0.6/1 kV (P5/P12) & BFOU(i)/(c) 250 V (S3/S7, S4/S8) | Fire-resistant (IEC 60331-21) emergency power, ESD and fire & gas cables adding mica glass fire-barrier tape over each conductor.
| RFOU Medium Voltage 3.6/6 kV – 12/20(24) kV (P2/P9, P3/P10, P19/P21) | Triple-extruded semiconductive conductor screen, EPR insulation and semiconductive insulation screen with TCWB armour and red SHF2 mud-resistant outer sheath.

## Series
NEK 606 BFOU & RFOU Mud-Resistant Offshore Cables – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NEK TS 606 / IEC 60092-353, -354, -376 & -360 (SHF2). Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
RFOU 0.6/1 kV (P1/P8) | Flame-Retardant LV Power & Control | 0.6/1 kV | NEK 606 P1 / P8 · IEC 60092-353 | 22 | Main LV distribution, motor feeders, lighting & general topside control
BFOU 0.6/1 kV (P5/P12) | Fire-Resistant LV Power & Control | 0.6/1 kV | NEK 606 P5 / P12 · IEC 60331-21 | 18 | Emergency generators, fire pumps, deluge valves & escape lighting
RFOU(i) / (c) 250 V (S1–S6) | Flame-Retardant Screened Instrumentation | 150/250 V | NEK 606 S1/S5 & S2/S6 · IEC 60092-376 | 14 | Process control, 4–20 mA transmitters, HART & DCS fieldbus
BFOU(i) / (c) 250 V (S3–S8) | Fire-Resistant Screened Instrumentation | 150/250 V | NEK 606 S3/S7 & S4/S8 · IEC 60331-21 | 14 | Emergency shutdown (ESD), fire & gas detection and PAGA loops
RFOU MV (P2/P3/P102) | Medium-Voltage Mud-Resistant Power | 3.6/6 kV & 6/10(12) kV | NEK 606 P2/P9 & P3/P10 · IEC 60092-354 | 15 | Main platform gas-turbine generators, HV switchboards & compressors

## Quality and supply
NEK 606 BFOU & RFOU Mud-Resistant Offshore Cables – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nek-606-bfou-rfou-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NEK TS 606 / IEC 60092-353, -354, -376 & -360 (SHF2). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & high-voltage AC dielectric test — 100 % drum verification of tinned copper DC resistance (IEC 60228) and AC withstand (3.5 kV for 0.6/1 kV; 1.5 kV for 250 V) | Every production length
Type test | Fire resistance / circuit integrity (BFOU — IEC 60331-21 / IEC 60331-11) — Maintains electrical continuity under 750 °C (or 830 °C with mechanical shock) flame for 90–180 minutes at rated voltage | Type approval & periodic audit (BFOU & BFOU(i)/(c))
Type test | Vertical bunched flame propagation (IEC 60332-3-22 Category A) — Charred portion ≤ 2.5 m above bottom edge of burner with 7 L/m non-metallic volume on vertical ladder | Type approval & periodic sample (all series)
Type test | NEK TS 606 drilling mud immersion (SHF2 mud-resistant) — Immersion in IRM 902/903 oil (100 °C, 7 d), calcium bromide brine (70 °C, 56 d) andEDC 95-11 / ester mud (70 °C, 56 d) within volume swell and tensile limits | Type approval
Type test | Halogen acid gas & smoke density (IEC 60754-1/2 & IEC 61034-1/2) — Halogen acid gas < 0.5 % HCl; pH ≥ 4.3, conductivity ≤ 10 µS/mm; minimum 60 % light transmittance in 3 m cube | Type approval
Standard / approval | NEK TS 606 (Codes P1/P8, P5/P12, S1–S8, P2/P9, P3/P10, P19/P21)
Standard / approval | IEC 60092-353 / -354 / -376 & IEC 60092-360 (SHF2 Mud)
Standard / approval | DNV, ABS, Lloyd's Register & Bureau Veritas Offshore Type Approval
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX — NEK 606 — <BFOU OR RFOU> — <VOLTAGE> — <NEK CODE> — <SIZE> — SHF2 MUD — IEC 60092 — IEC 60332-3-22 CAT A — [IEC 60331-21] — METRE MARK
Supply | Standard packing: 500 m or 1,000 m export seaworthy wooden drums
Supply | Outer sheath colours: Black (LV power); Red (MV power); Grey (non-Ex-i inst.); Blue (Ex-i inst.)
Supply | Conductor options: IEC 60228 Class 2 stranded tinned copper standard; Class 5 flexible to order
Supply | Export tariff code: HS 8544.49 (≤ 1,000 V) / HS 8544.60 (> 1,000 V)