## Request a quote
Request a quotation for NHXCH
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nhxch-fire-resistant-cable-with-concentric-conductor/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NHXCH Fire-Resistant Cable with Concentric Conductor – Dimensions & masses (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxch-fire-resistant-cable-with-concentric-conductor/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × mm² | Cross-section | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| NHXCH 2×1.5/1.5 RE FE180/E90 | 2×1.5/1.5 | 1.5 mm² | 12.5 | 52 | 220 | 150 | NHXCH standard series
| NHXCH 2×2.5/2.5 RE FE180/E90 | 2×2.5/2.5 | 2.5 mm² | 13.5 | 80 | 265 | 162 | NHXCH standard series
| NHXCH 3×1.5/1.5 RE FE180/E90 | 3×1.5/1.5 | 1.5 mm² | 13 | 66 | 245 | 156 | NHXCH standard series
| NHXCH 3×2.5/2.5 RE FE180/E90 | 3×2.5/2.5 | 2.5 mm² | 14 | 104 | 305 | 168 | NHXCH standard series
| NHXCH 4×1.5/1.5 RE FE180/E90 | 4×1.5/1.5 | 1.5 mm² | 13.8 | 81 | 280 | 166 | NHXCH standard series
| NHXCH 4×2.5/2.5 RE FE180/E90 | 4×2.5/2.5 | 2.5 mm² | 15 | 128 | 355 | 180 | NHXCH standard series
| NHXCH 4×4/4 RE FE180/E90 | 4×4/4 | 4.0 mm² | 16.5 | 200 | 460 | 198 | NHXCH standard series
| NHXCH 4×6/6 RE FE180/E90 | 4×6/6 | 6.0 mm² | 18 | 296 | 590 | 216 | NHXCH standard series
| NHXCH 4×10/10 RE FE180/E90 | 4×10/10 | 10 mm² | 20.2 | 488 | 825 | 242 | NHXCH standard series
| NHXCH 4×16/16 RM FE180/E90 | 4×16/16 | 16 mm² | 23.2 | 776 | 1180 | 278 | NHXCH standard series
| NHXCH 4×25/16 RM FE180/E90 | 4×25/16 | 25 mm² | 27.2 | 1136 | 1690 | 326 | NHXCH standard series
| NHXCH 4×35/16 RM FE180/E90 | 4×35/16 | 35 mm² | 30 | 1520 | 2140 | 360 | NHXCH standard series
| NHXCH 4×50/25 RM FE180/E90 | 4×50/25 | 50 mm² | 34.5 | 2200 | 2920 | 414 | NHXCH standard series
| NHXCH 4×70/35 RM FE180/E90 | 4×70/35 | 70 mm² | 39 | 3080 | 3980 | 468 | NHXCH standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per DIN VDE 0266 / DIN 4102-12.

## Electrical data
NHXCH Fire-Resistant Cable with Concentric Conductor – Electrical data (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxch-fire-resistant-cable-with-concentric-conductor/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Cores × mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2×1.5/1.5 | 12.1 | 24 | 21
2×2.5/2.5 | 7.41 | 32 | 28
3×1.5/1.5 | 12.1 | 21 | 18
3×2.5/2.5 | 7.41 | 28 | 24
4×1.5/1.5 | 12.1 | 21 | 18
4×2.5/2.5 | 7.41 | 28 | 24
4×4/4 | 4.61 | 37 | 32
4×6/6 | 3.08 | 48 | 41
4×10/10 | 1.83 | 66 | 57
4×16/16 | 1.15 | 88 | 76
4×25/16 | 0.727 | 117 | 101
4×35/16 | 0.524 | 144 | 124
4×50/25 | 0.387 | 175 | 150
4×70/35 | 0.268 | 222 | 191
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
NHXCH Fire-Resistant Cable with Concentric Conductor – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxch-fire-resistant-cable-with-concentric-conductor/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U AC power distribution)
Key data | Fire integrity | FE180 E30–E90 (180 min insulation / 30–90 min system)
Key data | Concentric screen | Cu wire + tape (Annealed copper wires + counter-helix)
Key data | Operating temp | -30 to +90 °C (Fixed installation (+250 °C short-circui)
Key data | Min. bend radius | 12 × cable OD (Fixed routing on E30/E90 trays)
Key data | Smoke & halogen | IEC 61034 / 6075 (LSZH HM4 sheath, ≥60 % transmittance)
Electrical | Nominal voltage U0/U | 0.6/1 kV
Electrical | Routine AC test voltage | 4.0 kV (50 Hz, 5 min)
Electrical | Max. operating voltage AC | 1.2 kV
Electrical | Concentric screen conductance | Matches rated geometric cross-section per IEC 60228
Thermal | Continuous conductor temp. | +90 °C max.
Thermal | Short-circuit conductor temp. | +250 °C (5 s)
Thermal | Fixed operating temp. | -30 °C to +90 °C
Mechanical | Min. bending radius (fixed) | 12 × cable OD
Mechanical | Max. pulling tension | 50 N/mm² on phase conductors
Mechanical | Impact & radial protection | Concentric Cu screen provides automatic fault disconnection on penetration
Resistance | Insulation integrity | FE180 (180 min @ ≥750 °C per IEC 60331-21)
Resistance | System circuit integrity | E30 / E90 per DIN 4102-12
Resistance | Flame propagation | IEC 60332-3-24 Cat. C / EN 60332-1-2
Resistance | Corrosivity & smoke | IEC 60754-2 (pH ≥4.3) & IEC 61034-2 (≥60 % light transmission)
Standards | Design standard | DIN VDE 0266
Standards | System fire endurance | DIN 4102-12
Identification | Core identification | HD 308 S2 without green/yellow (concentric screen serves as PE/PEN)
Identification | Outer sheath colour | Orange (RAL 2003)

## Construction
NHXCH Fire-Resistant Cable with Concentric Conductor – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxch-fire-resistant-cable-with-concentric-conductor/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Bare copper phase conductor | Solid (RE, 1.5–16 mm²) or stranded (RM, 16–240 mm²) copper per IEC 60228 | IEC 60228
2 | Mica-glass fire barrier | Double helically lapped phlogopite mica tape over each conductor (FE180) | IEC 60331-21
3 | Cross-linked LSZH insulation | Halogen-free cross-linked polymer compound type HX | DIN VDE 0266
4 | Inner halogen-free bedding | Flame-retardant mineral-filled LSZH inner extruded jacket | DIN VDE 0266
5 | Concentric copper conductor | Helical layer of bare copper wires with copper counter-helix equalizer tape | DIN VDE 0266
6 | Outer LSZH safety sheath | Halogen-free thermoplastic polyolefin compound HM4, orange (RAL 2003) | DIN VDE 0266
| NHXCH FE180/E30 | Concentric copper conductor rated for 30-minute functional circuit integrity per DIN 4102-12.
| NHXCH FE180/E90 | Concentric copper conductor rated for 90-minute functional circuit integrity for fire pumps and lifts.

## Quality and supply
NHXCH Fire-Resistant Cable with Concentric Conductor – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxch-fire-resistant-cable-with-concentric-conductor/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 4.0 kV AC dielectric withstand test — 5 minutes between cores and concentric copper screen without breakdown | 100 % of drums
Routine test | Phase & concentric conductor DC resistance — Verified at 20 °C per IEC 60228 / DIN VDE 0266 | 100 % of drums
Type test | FE180 direct flame circuit integrity — ≥180 min at ≥750 °C per IEC 60331-21 | Type approval
Type test | DIN 4102-12 furnace survival E30–E90 — 30–90 minutes complete system function up to 1000 °C | Type approval
Standard / approval | DIN VDE 0266
Standard / approval | DIN 4102-12 E30–E90
Standard / approval | IEC 60331-21 FE180
Standard / approval | IEC 60332-3-24 Cat. C
Standard / approval | IEC 60754-2 & IEC 61034-2
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NHXCH 4x16/16 RM FE180/E90 0.6/1 kV DIN VDE 0266 DIN 4102-12 CE [year] [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP