## Request a quote
Request a quotation for NHXH
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nhxh-halogen-free-fire-resistant-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NHXH Halogen-Free Fire-Resistant Power Cable – Dimensions & masses (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxh-halogen-free-fire-resistant-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × mm² | Cross-section | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| NHXH-O 1×16 RM FE180/E90 | 1×16 RM | 16 mm² | 10.5 | 154 | 240 | 126 | NHXH standard series
| NHXH-O 1×35 RM FE180/E90 | 1×35 RM | 35 mm² | 13 | 336 | 445 | 156 | NHXH standard series
| NHXH-O 1×50 RM FE180/E90 | 1×50 RM | 50 mm² | 14.5 | 480 | 600 | 174 | NHXH standard series
| NHXH-O 1×95 RM FE180/E90 | 1×95 RM | 95 mm² | 18.2 | 912 | 1080 | 218 | NHXH standard series
| NHXH-J 3×1.5 RE FE180/E90 | 3×1.5 RE | 1.5 mm² | 11.5 | 43 | 185 | 138 | NHXH standard series
| NHXH-J 3×2.5 RE FE180/E90 | 3×2.5 RE | 2.5 mm² | 12.5 | 72 | 230 | 150 | NHXH standard series
| NHXH-J 4×1.5 RE FE180/E90 | 4×1.5 RE | 1.5 mm² | 12.4 | 58 | 215 | 149 | NHXH standard series
| NHXH-J 4×2.5 RE FE180/E90 | 4×2.5 RE | 2.5 mm² | 13.5 | 96 | 275 | 162 | NHXH standard series
| NHXH-J 4×4 RE FE180/E90 | 4×4 RE | 4.0 mm² | 15 | 154 | 370 | 180 | NHXH standard series
| NHXH-J 4×6 RE FE180/E90 | 4×6 RE | 6.0 mm² | 16.5 | 230 | 485 | 198 | NHXH standard series
| NHXH-J 4×10 RE FE180/E90 | 4×10 RE | 10 mm² | 18.5 | 384 | 695 | 222 | NHXH standard series
| NHXH-J 4×16 RM FE180/E90 | 4×16 RM | 16 mm² | 21.5 | 614 | 990 | 258 | NHXH standard series
| NHXH-J 4×25 RM FE180/E90 | 4×25 RM | 25 mm² | 25.5 | 960 | 1480 | 306 | NHXH standard series
| NHXH-J 4×35 RM FE180/E90 | 4×35 RM | 35 mm² | 28.2 | 1344 | 1920 | 338 | NHXH standard series
| NHXH-J 5×1.5 RE FE180/E90 | 5×1.5 RE | 1.5 mm² | 13.2 | 72 | 250 | 158 | NHXH standard series
| NHXH-J 5×2.5 RE FE180/E90 | 5×2.5 RE | 2.5 mm² | 14.5 | 120 | 325 | 174 | NHXH standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per DIN VDE 0266 / DIN 4102-12.

## Electrical data
NHXH Halogen-Free Fire-Resistant Power Cable – Electrical data (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxh-halogen-free-fire-resistant-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Cores × mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
1×16 RM | 1.15 | 98 | 84
1×35 RM | 0.524 | 158 | 136
1×50 RM | 0.387 | 192 | 165
1×95 RM | 0.193 | 292 | 251
3×1.5 RE | 12.1 | 23 | 20
3×2.5 RE | 7.41 | 31 | 27
4×1.5 RE | 12.1 | 21 | 18
4×2.5 RE | 7.41 | 28 | 24
4×4 RE | 4.61 | 37 | 32
4×6 RE | 3.08 | 48 | 41
4×10 RE | 1.83 | 66 | 57
4×16 RM | 1.15 | 88 | 76
4×25 RM | 0.727 | 117 | 101
4×35 RM | 0.524 | 144 | 124
5×1.5 RE | 12.1 | 21 | 18
5×2.5 RE | 7.41 | 28 | 24
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
NHXH Halogen-Free Fire-Resistant Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxh-halogen-free-fire-resistant-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U AC power distribution)
Key data | Fire integrity | FE180 E30–E90 (180 min insulation / 30–90 min system)
Key data | Conductor | Cu Class 1 / 2 (Bare annealed copper per IEC 60228)
Key data | Operating temp | -30 to +90 °C (Fixed installation (+250 °C short-circui)
Key data | Min. bend radius | 12×D / 15×D (Multi-core 12×D · single-core 15×D)
Key data | Smoke & halogen | IEC 61034 / 6075 (Zero halogen, ≥60 % light transmittance)
Electrical | Nominal voltage U0/U | 0.6/1 kV
Electrical | Max. operating voltage AC | 1.2 kV
Electrical | Routine AC test voltage | 4.0 kV (50 Hz, 5 min)
Electrical | Insulation resistance @ 20 °C | ≥100 MΩ·km
Thermal | Continuous conductor temp. | +90 °C max.
Thermal | Short-circuit conductor temp. | +250 °C (max. 5 s)
Thermal | Fixed operating range | -30 °C to +90 °C
Thermal | Min. installation temp. | -5 °C
Mechanical | Min. bend radius (multi-core) | 12 × cable OD
Mechanical | Min. bend radius (single-core) | 15 × cable OD
Mechanical | Max. pulling tension | 50 N/mm² of total Cu cross-section
Resistance | Insulation integrity in fire | FE180 (180 min @ ≥750 °C per IEC 60331-21 / VDE 0472-814)
Resistance | System circuit integrity | E30 / E60 / E90 per DIN 4102-12 on certified support systems
Resistance | Bunched vertical flame spread | IEC 60332-3-24 Cat. C / EN 60332-1-2
Resistance | Halogen acidity & conductivity | pH ≥4.3, conductivity ≤10 µS/mm per IEC 60754-2
Standards | Construction standard | DIN VDE 0266
Standards | System fire test standard | DIN 4102-12
Standards | Smoke density standard | IEC 61034-2 (light transmittance ≥60 %)
Identification | Core colour code | HD 308 S2 / DIN VDE 0293-308 (-J with GN/YE, -O without)
Identification | Outer sheath colour | Orange (RAL 2003)

## Construction
NHXH Halogen-Free Fire-Resistant Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxh-halogen-free-fire-resistant-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Bare copper conductor | Solid (RE, 1.5–16 mm²) or stranded (RM, 16–240 mm²) annealed copper, Class 1/2 | IEC 60228
2 | Fire barrier lapped tape | Double phlogopite mica-glass flame barrier tape (FE180) | IEC 60331-21
3 | Cross-linked LSZH insulation | Halogen-free cross-linked polymer compound (HX) or ceramifying silicone | DIN VDE 0266
4 | Halogen-free inner filling | Flame-retardant mineral-filled LSZH extruded inner bedding | DIN VDE 0266
5 | Outer safety sheath | Thermoplastic halogen-free polyolefin compound type HM4, orange (RAL 2003) | DIN VDE 0266
| NHXH-J FE180/E30 | With green/yellow protective conductor, 30-minute system circuit integrity per DIN 4102-12.
| NHXH-J FE180/E90 | With green/yellow protective conductor, 90-minute system circuit integrity for firefighting lifts and smoke vents.
| NHXH-O FE180/E90 | Without green/yellow conductor for isolated IT safety power supplies and DC emergency battery feeders.

## Quality and supply
NHXH Halogen-Free Fire-Resistant Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nhxh-halogen-free-fire-resistant-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0266 / DIN 4102-12. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Spark & 4.0 kV AC dielectric voltage test — No breakdown at 4.0 kV rms for 5 minutes | 100 % of manufacturing lengths
Routine test | Conductor DC resistance verification — Conforms to IEC 60228 Class 1 / Class 2 limits at 20 °C | 100 % of drums
Type test | Insulation integrity under direct flame (FE180) — ≥180 min at ≥750 °C under rated voltage per IEC 60331-21 | Type qualification
Type test | System circuit integrity in furnace (E30 / E90) — 30 to 90 min up to 1000 °C per DIN 4102-12 on tested brackets | Type qualification
Standard / approval | DIN VDE 0266
Standard / approval | DIN 4102-12 E30–E90
Standard / approval | IEC 60331-21 FE180
Standard / approval | IEC 60332-3-24 Cat. C
Standard / approval | IEC 60754-1/2 & IEC 61034-2
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NHXH-J 4x16 RM FE180/E90 0.6/1 kV DIN VDE 0266 DIN 4102-12 CE [year] [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP