## Request a quote
Request a quotation for NSGAFCMÖU
Mining & railway switchgear cable engineer
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nsgafcmoeu-screened-rubber-insulated-single-core-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NSGAFCMÖU Screened Rubber-Insulated Single-Core Wire – Phase/screen sizes, OD, weight & ampacity (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafcmoeu-screened-rubber-insulated-single-core-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / VDE 0100-520 / VDE 0118. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Phase / Screen mm² | Phase R @20°C Ω/km | EPR Core OD mm | Overall OD mm | Weight kg/km | Ampacity A (30°C) | Fixed R mm | Series
| NSGAFCMOEU-1X1.5/1.5 | 1 × 1.5 / 1.5 | 13.7 | 5 | 9.2 | 115 | 30 | 46 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X2.5/1.5 | 1 × 2.5 / 1.5 | 8.21 | 5.5 | 9.8 | 135 | 41 | 49 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X4/2.5 | 1 × 4.0 / 2.5 | 5.09 | 6 | 10.6 | 168 | 55 | 53 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X6/2.5 | 1 × 6.0 / 2.5 | 3.39 | 6.5 | 11.2 | 198 | 70 | 56 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X10/4 | 1 × 10 / 4.0 | 1.95 | 7.5 | 12.6 | 265 | 98 | 63 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X16/6 | 1 × 16 / 6.0 | 1.24 | 8.8 | 14.2 | 355 | 132 | 71 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X25/6 | 1 × 25 / 6.0 | 0.795 | 10.5 | 16 | 475 | 176 | 80 | Screened Control & Auxiliary Feeder Sizes — 1×1.5/1.5 mm² to 1×25/6 mm²
| NSGAFCMOEU-1X35/6 | 1 × 35 / 6.0 | 0.565 | 11.8 | 17.5 | 595 | 218 | 88 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
| NSGAFCMOEU-1X50/10 | 1 × 50 / 10 | 0.393 | 13.6 | 19.6 | 810 | 276 | 98 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
| NSGAFCMOEU-1X70/10 | 1 × 70 / 10 | 0.277 | 15.5 | 21.8 | 1045 | 347 | 109 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
| NSGAFCMOEU-1X95/16 | 1 × 95 / 16 | 0.21 | 17.8 | 24.5 | 1365 | 416 | 123 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
| NSGAFCMOEU-1X120/16 | 1 × 120 / 16 | 0.164 | 19.6 | 26.5 | 1640 | 488 | 133 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
| NSGAFCMOEU-1X185/25 | 1 × 185 / 25 | 0.108 | 23.8 | 31.4 | 2420 | 644 | 157 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
| NSGAFCMOEU-1X240/35 | 1 × 240 / 35 | 0.082 | 26.8 | 35 | 3120 | 764 | 175 | Screened Switchgear, VFD & Traction Power Sizes — 1×35/6 mm² to 1×240/35 mm²
When installing single-core screened cables in 3-phase AC circuits, bond the concentric copper screens at one end (or via cross-bonding) if circulating sheath currents exceed thermal limits.

## Technical data
NSGAFCMÖU Screened Rubber-Insulated Single-Core Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafcmoeu-screened-rubber-insulated-single-core-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / VDE 0100-520 / VDE 0118. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | VDE 0250-602 (NSGAFCMÖU 1.8/3 (3.6) kV AC)
Key data | DC voltage | Up to 5.4 kV DC (2.7/5.4 kV DC traction & mining)
Key data | Concentric screen | Tinned Cu (CM) (Fault-current & EMC copper screen)
Key data | Cross-section | 1.5/1.5–240/35 (Phase / screen mm² combinations)
Key data | Insulation | 3GI3 EPR (+90°C) (+250 °C short-circuit rating)
Key data | Outer sheath | 5GM2 Elastomer (Oil-resistant & flame-retardant)
Electrical | Nominal AC voltage (U0/U) | 1.8/3 kV · Max operating Um = 3.6 kV AC
Electrical | Max. operating DC voltage | 2.7/5.4 kV DC
Electrical | AC test voltage (core to screen) | 6.0 kV AC rms for 5 min
Electrical | AC test voltage (screen to water) | 2.0 kV AC rms for 5 min
Electrical | Max. conductor temperature | +90 °C continuous · +250 °C short-circuit
Thermal | Operating temperature (fixed) | −40 °C to +80 °C
Thermal | Operating temperature (flexing) | −25 °C to +80 °C
Mechanical | Phase / screen sizes | 1×1.5/1.5 mm² up to 1×240/35 mm²
Mechanical | Min. bend radius | 5 × OD (fixed) · 10 × OD (flexible installation)
Resistance | Oil resistance (Ö) | DIN EN 60811-404 (IRM 902 oil at 100 °C)
Resistance | Flame retardancy (U) | DIN EN 60332-1-2
Resistance | Ozone & weather | DIN VDE 0250-602 ozone & moisture resistant
Standards | Primary specification | DIN VDE 0250-602
Standards | Installation rules | DIN VDE 0100-520 · DIN VDE 0118 (mining) ·DIN VDE 0298-4
Identification | Outer sheath colour | Black (Polychloroprene 5GM2)
Identification | Surface legend | TEBAOFLEX NSGAFCMÖU 1.8/3 kV [MM2/MM2] VDE 0250-602
Identification | Customs tariff (HS) | 8544.60

## Construction
NSGAFCMÖU Screened Rubber-Insulated Single-Core Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafcmoeu-screened-rubber-insulated-single-core-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / VDE 0100-520 / VDE 0118. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded Class 5 tinned copper phase conductor | Annealed tinned copper wires to DIN EN 60228 / VDE 0295 Class 5 (1.5 mm² to 240 mm²)
2 | 1.8/3 kV EPR (3GI3) dielectric | Cross-linked ethylene propylene rubber (EPR compound 3GI3 to DIN VDE 0207-20) rated +90 °C continuous and +250 °C short-circuit
3 | Inner elastomer bedding / semiconductive tape | Thin inner rubber bedding or conductive tape layer over the EPR core
4 | Concentric tinned copper screen (CM) | Helically lapped or braided tinned copper wires (1.5 mm² to 35 mm² geometric screen cross-section, ≥ 85 % coverage)
5 | Heavy-duty 5GM2 polychloroprene outer sheath (ÖU) | Oil-resistant (`Ö`) and flame-retardant (`U`) black polychloroprene elastomer outer jacket (compound 5GM2 to DIN VDE 0207-21)
| NSGAFCMÖU-CTRL (1.5/1.5 to 16/6 mm² Control & CT) | Screened 1.8/3 kV single-core wire for intrinsically safe / earth-monitored mining control panels and PT/CT secondary leads
| NSGAFCMÖU-PWR (25/6 to 240/35 mm² Inverter & Bus) | Heavy screened single-core power leads for 690 V–3.3 kV VFD motor connections, traction converters and mining transformers

## Quality and supply
NSGAFCMÖU Screened Rubber-Insulated Single-Core Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafcmoeu-screened-rubber-insulated-single-core-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / VDE 0100-520 / VDE 0118. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 6.0 kV AC core-to-screen & 2.0 kV AC screen-to-water test — 5-minute wet/dry AC dielectric withstand test on every length | 100 % of manufactured reels
Routine test | Phase & concentric screen DC resistance test — Verify Class 5 conductor and CM screen cross-sectional conductivity | 100 % of manufactured reels
Type test | 5GM2 oil immersion & IEC 60332-1-2 flame propagation — Verify oil-resistant (`Ö`) and flame-retardant (`U`) sheath compliance | Type approval
Standard / approval | DIN VDE 0250-602 NSGAFCMÖU 1.8/3 kV Compliant
Standard / approval | DIN VDE 0118 Mining & VDE 0100-520 Short-Circuit Proof
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NSGAFCMÖU 1.8/3 kV [MM2/MM2] VDE 0250-602
Supply | Delivery form: 100 m coils or 500 m / 1,000 m wooden drums
Supply | Accessories: EMC brass/stainless compression glands & screen earthing kits
Supply | Lead time: 2–4 weeks ex-works