## Request a quote
Request a quotation for NSGAFÖU 1.8/3 kV
Application engineer · switchgear & rail cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nsgafoeu-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NSGAFÖU 1.8/3 kV Short-Circuit-Proof Single-Core Rubber Wire – Dimensions & weights (18)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / IEC 60228. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section mm² | 3GI3 wall mm | 5GM3 wall mm | OD min mm | OD nom mm | OD max mm | Cu weight kg/km | Total weight ≈ kg/km | Ampacity (air) A | Series
| NSGAFÖU 1 × 1.5 | 1 × 1.5 | 1.3 | 0.8 | 5.1 | 6.3 | 7 | 14 | 51 | 30 | 1.5 – 16 mm²
| NSGAFÖU 1 × 2.5 | 1 × 2.5 | 1.3 | 0.8 | 5.6 | 6.7 | 7.5 | 24 | 63 | 41 | 1.5 – 16 mm²
| NSGAFÖU 1 × 4 | 1 × 4 | 1.3 | 0.8 | 6.2 | 7.4 | 9 | 38 | 82 | 55 | 1.5 – 16 mm²
| NSGAFÖU 1 × 6 | 1 × 6 | 1.3 | 0.8 | 6.7 | 7.9 | 9.5 | 58 | 103 | 70 | 1.5 – 16 mm²
| NSGAFÖU 1 × 10 | 1 × 10 | 1.5 | 0.8 | 8.1 | 9.5 | 11 | 96 | 159 | 98 | 1.5 – 16 mm²
| NSGAFÖU 1 × 16 | 1 × 16 | 1.5 | 0.8 | 9.1 | 10.5 | 13 | 154 | 219 | 132 | 1.5 – 16 mm²
| NSGAFÖU 1 × 25 | 1 × 25 | 1.6 | 1 | 11.1 | 12.8 | 15 | 240 | 335 | 176 | 25 – 120 mm²
| NSGAFÖU 1 × 35 | 1 × 35 | 1.6 | 1 | 12.3 | 14.1 | 16.5 | 336 | 435 | 218 | 25 – 120 mm²
| NSGAFÖU 1 × 50 | 1 × 50 | 1.8 | 1 | 13.8 | 15.9 | 18 | 480 | 582 | 276 | 25 – 120 mm²
| NSGAFÖU 1 × 70 | 1 × 70 | 1.8 | 1 | 15.5 | 17.8 | 20.5 | 672 | 757 | 347 | 25 – 120 mm²
| NSGAFÖU 1 × 95 | 1 × 95 | 2.2 | 1 | 17.7 | 20.1 | 24 | 912 | 1040 | 416 | 25 – 120 mm²
| NSGAFÖU 1 × 120 | 1 × 120 | 2.2 | 1 | 19.2 | 22 | 26 | 1152 | 1289 | 488 | 25 – 120 mm²
| NSGAFÖU 1 × 150 | 1 × 150 | 2.2 | 1.2 | 21.1 | 24 | 28 | 1440 | 1581 | 566 | 150 – 500 mm²
| NSGAFÖU 1 × 185 | 1 × 185 | 2.4 | 1.2 | 23.1 | 26.3 | 31 | 1776 | 1895 | 644 | 150 – 500 mm²
| NSGAFÖU 1 × 240 | 1 × 240 | 2.6 | 1.2 | 26 | 29.6 | 34.5 | 2304 | 2452 | 775 | 150 – 500 mm²
| NSGAFÖU 1 × 300 | 1 × 300 | 2.8 | 1.2 | 28.4 | 32.2 | 38 | 2880 | 2998 | 898 | 150 – 500 mm²
| NSGAFÖU 1 × 400 | 1 × 400 | 3.1 | 1.4 | 34.6 | 40.5 | 41.5 | 3840 | 4200 | 1060 | 150 – 500 mm²
| NSGAFÖU 1 × 500 | 1 × 500 | 3.4 | 1.6 | 38 | 42 | 45 | 4800 | 5500 | 1250 | 150 – 500 mm²
Current ratings apply to single-core routing in free air at 30 °C ambient and 90 °C conductor temperature.

## Resistance & ampacity
NSGAFÖU 1.8/3 kV Short-Circuit-Proof Single-Core Rubber Wire – Resistance & ampacity (18)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / IEC 60228. Values for your order are confirmed in the quotation.
Cross-section mm² | Max. DC resistance at 20 °C (tinned) Ω/km | Current in free air (30 °C) A | Current in conduit (30 °C) A | Max. pulling load (15 N/mm²) N
1 × 1.5 | 13.7 | 30 | 15 | 22
1 × 2.5 | 8.21 | 41 | 21 | 38
1 × 4 | 5.09 | 55 | 29 | 60
1 × 6 | 3.39 | 70 | 37 | 90
1 × 10 | 1.95 | 98 | 52 | 150
1 × 16 | 1.24 | 132 | 70 | 240
1 × 25 | 0.795 | 176 | 93 | 375
1 × 35 | 0.565 | 218 | 115 | 525
1 × 50 | 0.393 | 276 | 146 | 750
1 × 70 | 0.277 | 347 | 185 | 1050
1 × 95 | 0.21 | 416 | 221 | 1425
1 × 120 | 0.164 | 488 | 259 | 1800
1 × 150 | 0.132 | 566 | 301 | 2250
1 × 185 | 0.108 | 644 | 342 | 2775
1 × 240 | 0.0817 | 775 | 412 | 3600
1 × 300 | 0.0654 | 898 | 467 | 4500
1 × 400 | 0.0486 | 1060 | 557 | 6000
1 × 500 | 0.0384 | 1250 | 662 | 7500
Conductor resistance values comply with IEC 60228 Class 5 metal-coated (tinned) copper conductors at 20 °C.

## Technical data
NSGAFÖU 1.8/3 kV Short-Circuit-Proof Single-Core Rubber Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / IEC 60228. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 kV (Max 2.1/3.6 kV AC · 2.7/5.4 kV DC)
Key data | Short-circuit duty | Up to 1,000 V (Switchgear & distribution boards)
Key data | Core / sheath | 3GI3 EPR / 5GM3 (DIN VDE 0207-20 / 0207-21)
Key data | Min. bend R | 4–6 × D fixed (5–10 × D flexing)
Key data | Operating temp. | -25 to +80 °C (-40 to +80 °C fixed (+90 °C Cu))
Key data | Test voltage | 6 kV AC (Routine dielectric test)
Electrical | Rated voltage U0/U (max AC / DC) | 1.8/3 kV AC nominal · max. 2.1/3.6 kV AC · max. 2.7/5.4 kV DC
Electrical | Test voltage & short-circuit proof rating | 6.0 kV AC routine test · Short-circuit & earth-fault proof in switchgear up to 1,000 V
Thermal | Ambient temperature — flexing / fixed | -25 to +80 °C flexing · -40 to +80 °C fixed (up to +90 °C at conductor)
Thermal | Max. short-circuit conductor temperature | +250 °C (max. 5 s)
Mechanical | Min. bending radius | 4 × D to 6 × D fixed installation · 5 × D to 10 × D flexing / moving
Mechanical | Permissible tensile load | 15 N/mm² of copper cross-section during installation (22.5 N on 1.5 mm² to 7,500 N on 500 mm²)
Standards | Reference standards | DIN VDE 0250-602 · DIN VDE 0295 / IEC 60228 Class 5 · DIN VDE 0207-20 (3GI3) · DIN VDE 0207-21 (5GM3)
Standards | Flame & oil resistance | Flame-retardant IEC 60332-1-2 (VDE 0482-332-1-2) · Oil-resistant EN 60811-404 (VDE 0473-811-404)

## Construction
NSGAFÖU 1.8/3 kV Short-Circuit-Proof Single-Core Rubber Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / IEC 60228. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductor | Fine-stranded tinned annealed copper, Class 5 per DIN VDE 0295 / IEC 60228
2 | Core insulation (3GI3) | Ethylene-propylene rubber compound type 3GI3 per DIN VDE 0207-20
3 | Outer sheath (5GM3) | Oil-resistant, flame-retardant polychloroprene rubber compound type 5GM3, black
| NSGAFÖU 1.8/3 kV Black (1×1.5 – 1×500 mm²) | Standard black 5GM3 polychloroprene outer sheath over 3GI3 EPR insulation for switchgear and rail wiring
| NSGAFÖU 1.8/3 kV Orange (1×1.5 – 1×300 mm²) | Optional high-visibility orange 5GM3 outer sheath for HV traction and DC busbar identification

## Quality and supply
NSGAFÖU 1.8/3 kV Short-Circuit-Proof Single-Core Rubber Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsgafoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-602 / IEC 60228. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC spark / dielectric voltage test — 6.0 kV AC | Every production length
Routine test | Conductor DC resistance at 20 °C — DIN VDE 0295 / IEC 60228 Class 5 (tinned) | Every production length
Sample test | Vertical flame propagation — IEC 60332-1-2 (VDE 0482-332-1-2) | Per production batch
Type test | Oil resistance of 5GM3 outer sheath — EN 60811-404 (VDE 0473-811-404) | Per compound batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NSGAFÖU 1.8/3 kV [1×mm²] · DIN VDE 0250-602 · CE · [year] · [metre mark]
Supply | Standard packing: Coils (small cross-sections) or non-returnable/returnable wooden drums
Supply | HS code: 8544.60
Supply | Minimum order: None
Supply | Lead time: None