## Request a quote
Request a quotation for NSHXAFÖ 1.8/3 kV
Application engineer · switchgear & rail cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nshxafoe-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NSHXAFÖ 1.8/3 kV Halogen-Free Short-Circuit-Proof Single-Core Wire – 1.8/3 kV dimensions & weights (18)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxafoe-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-606 / VDE 0250-602. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section mm² | OD min mm | OD approx mm | OD max mm | Cu weight kg/km | Total weight ≈ kg/km | Max. pull N | Ampacity (air) A | Series
| NSHXAFÖ 1 × 1.5 | 1 × 1.5 | 5.7 | 6 | 7 | 14 | 50 | 21 | 30 | 1.5 – 16 mm²
| NSHXAFÖ 1 × 2.5 | 1 × 2.5 | 6 | 6.5 | 7.5 | 24 | 60 | 41 | 41 | 1.5 – 16 mm²
| NSHXAFÖ 1 × 4 | 1 × 4 | 6.8 | 7 | 9 | 38 | 80 | 60 | 55 | 1.5 – 16 mm²
| NSHXAFÖ 1 × 6 | 1 × 6 | 7.3 | 7.5 | 9.5 | 58 | 100 | 90 | 70 | 1.5 – 16 mm²
| NSHXAFÖ 1 × 10 | 1 × 10 | 8.7 | 9 | 11 | 96 | 160 | 150 | 98 | 1.5 – 16 mm²
| NSHXAFÖ 1 × 16 | 1 × 16 | 10 | 10.5 | 13 | 154 | 230 | 240 | 132 | 1.5 – 16 mm²
| NSHXAFÖ 1 × 25 | 1 × 25 | 12.4 | 12.5 | 15 | 240 | 340 | 375 | 176 | 25 – 120 mm²
| NSHXAFÖ 1 × 35 | 1 × 35 | 13.4 | 13.5 | 16.5 | 336 | 430 | 525 | 219 | 25 – 120 mm²
| NSHXAFÖ 1 × 50 | 1 × 50 | 14.9 | 15.5 | 18 | 480 | 580 | 750 | 276 | 25 – 120 mm²
| NSHXAFÖ 1 × 70 | 1 × 70 | 16.6 | 17.5 | 20.5 | 672 | 780 | 1050 | 347 | 25 – 120 mm²
| NSHXAFÖ 1 × 95 | 1 × 95 | 19.3 | 20.5 | 24 | 912 | 1030 | 1425 | 416 | 25 – 120 mm²
| NSHXAFÖ 1 × 120 | 1 × 120 | 20.8 | 21.5 | 26 | 1152 | 1270 | 1800 | 488 | 25 – 120 mm²
| NSHXAFÖ 1 × 150 | 1 × 150 | 23 | 23.5 | 28 | 1440 | 1570 | 2250 | 566 | 150 – 500 mm²
| NSHXAFÖ 1 × 185 | 1 × 185 | 25.2 | 25.5 | 31 | 1776 | 1900 | 2775 | 644 | 150 – 500 mm²
| NSHXAFÖ 1 × 240 | 1 × 240 | 28.1 | 28 | 34.5 | 2304 | 2500 | 3600 | 775 | 150 – 500 mm²
| NSHXAFÖ 1 × 300 | 1 × 300 | 30.8 | 31.5 | 38 | 2890 | 3000 | 4500 | 898 | 150 – 500 mm²
| NSHXAFÖ 1 × 400 | 1 × 400 | 34.6 | 37.3 | 40 | 3840 | 4000 | 6000 | 1060 | 150 – 500 mm²
| NSHXAFÖ 1 × 500 | 1 × 500 | 39 | 43.5 | 45 | 4800 | 5860 | 7500 | 1250 | 150 – 500 mm²
1×400 mm² min/max OD corrected from transposed 40.0/34.6 mm in the PDF table to 34.6–40.0 mm.

## Resistance & 1 s short-circuit
NSHXAFÖ 1.8/3 kV Halogen-Free Short-Circuit-Proof Single-Core Wire – Resistance & 1 s short-circuit current (18)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxafoe-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-606 / VDE 0250-602. Values for your order are confirmed in the quotation.
Cross-section mm² | Max. DC resistance at 20 °C Ω/km | Current in air (30 °C) A | 1 s short-circuit current Ik kA | Max. pulling force N
1 × 1.5 | 13.7 | 30 | 0.21 | 21
1 × 2.5 | 8.21 | 41 | 0.35 | 41
1 × 4 | 5.09 | 55 | 0.57 | 60
1 × 6 | 3.39 | 70 | 0.85 | 90
1 × 10 | 1.95 | 98 | 1.43 | 150
1 × 16 | 1.24 | 132 | 2.28 | 240
1 × 25 | 0.795 | 176 | 3.57 | 375
1 × 35 | 0.565 | 219 | 5 | 525
1 × 50 | 0.393 | 276 | 7.15 | 750
1 × 70 | 0.277 | 347 | 10.01 | 1050
1 × 95 | 0.21 | 416 | 13.58 | 1425
1 × 120 | 0.164 | 488 | 17.16 | 1800
1 × 150 | 0.132 | 566 | 21.45 | 2250
1 × 185 | 0.108 | 644 | 26.45 | 2775
1 × 240 | 0.0817 | 775 | 34.32 | 3600
1 × 300 | 0.0654 | 898 | 42.9 | 4500
1 × 400 | 0.0486 | 1060 | 57.2 | 6000
1 × 500 | 0.0391 | 1250 | 71.5 | 7500
Adiabatic 1 s short-circuit current Ik is calculated for 90 °C initial to 250 °C final conductor temperature.

## 3.6 6 kV series dimensions
NSHXAFÖ 1.8/3 kV Halogen-Free Short-Circuit-Proof Single-Core Wire – 3.6/6 kV series dimensions (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxafoe-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-606 / VDE 0250-602. Values for your order are confirmed in the quotation.
Cross-section (3.6/6 kV) | OD min mm | OD max mm | Nominal weight ≈ kg/km
1 × 1.5 (3.6/6 kV) | 8.3 | 9.5 | 135
1 × 2.5 (3.6/6 kV) | 8.6 | 10.5 | 150
1 × 4 (3.6/6 kV) | 9.4 | 12 | 170
1 × 6 (3.6/6 kV) | 9.9 | 13 | 200
1 × 10 (3.6/6 kV) | 10.9 | 14.5 | 250
1 × 16 (3.6/6 kV) | 12.6 | 15.5 | 350
1 × 25 (3.6/6 kV) | 14.5 | 17.5 | 480
1 × 35 (3.6/6 kV) | 15.6 | 19 | 600
1 × 50 (3.6/6 kV) | 17.1 | 21 | 760
1 × 70 (3.6/6 kV) | 18.8 | 23 | 960
1 × 95 (3.6/6 kV) | 21.3 | 26.5 | 1240
1 × 120 (3.6/6 kV) | 23.2 | 28.5 | 1530
1 × 150 (3.6/6 kV) | 25 | 30.5 | 1790
1 × 185 (3.6/6 kV) | 26.8 | 33 | 2130
3.6/6 kV sizes include an inner semi-conductive conductor screen; screened NSHXAFCMÖ 1×185 mm² (3.6/6 kV) has 38.5 mm nominal OD and 3,060 kg/km weight.

## Technical data
NSHXAFÖ 1.8/3 kV Halogen-Free Short-Circuit-Proof Single-Core Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxafoe-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-606 / VDE 0250-602. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 & 3.6/6 kV (Max 2.7/5.4 kV DC (1.8/3 kV))
Key data | Halogen-free | IEC 60754/61034 (LSZH / FRNC · CPR Eca)
Key data | Core / sheath | 3GI3 EPR / HM3 (3GI3 EPR + HM3 FRNC jacket)
Key data | Short-circuit duty | Up to 1,000 V (Switchgear & rail cabinets)
Key data | Operating temp. | -25 to +70 °C (-40 to +70 °C fixed (+90 °C Cu))
Key data | Test voltage | 6 kV AC (Routine dielectric test)
Electrical | Rated voltage U0/U (max DC) | 1.8/3 kV AC standard (max. 2.7/5.4 kV DC) · 3.6/6 kV AC series also available
Electrical | Routine test voltage & short-circuit proof | 6.0 kV AC test (1.8/3 kV) · Inherently short-circuit & earth-fault proof up to 1,000 V
Thermal | Ambient temperature — moved / fixed | -25 to +70 °C moved · -40 to +70 °C fixed (conductor up to +90 °C)
Thermal | Max. short-circuit temperature | +250 °C (1 s adiabatic short-circuit rating 0.21 kA on 1.5 mm² to 71.5 kA on 500 mm²)
Mechanical | Min. bending radius | 6 × D fixed installation · 10 × D moving application (4 × D / 5 × D in dry cabinet wiring)
Mechanical | Permissible tensile load | 15 N/mm² of copper cross-section (21 N on 1.5 mm² up to 7,500 N on 500 mm²)
Standards | Reference standards | DIN VDE 0250-606 (halogen-free NSHXAFÖ) & DIN VDE 0250-602 · DIN EN IEC 60228 (VDE 0295) Class 5
Standards | Halogen-free, smoke, flame & oil performance | Halogen-free IEC 60754 (EN 50267) · Low smoke IEC 61034 · Flame-retardant IEC 60332-1-2 · Oil-resistant EN 60811-404 · CPR Eca

## Construction
NSHXAFÖ 1.8/3 kV Halogen-Free Short-Circuit-Proof Single-Core Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxafoe-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-606 / VDE 0250-602. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductor | Fine-stranded tinned annealed copper, Class 5 per DIN EN IEC 60228 (VDE 0295)
2 | Core insulation (3GI3) | Halogen-free ethylene-propylene rubber (EPR) compound type 3GI3 (3.6/6 kV series includes inner semi-conductive layer)
3 | Outer sheath (HM3) | Halogen-free, low-smoke flame-retardant cross-linked polymer compound type HM3, black
| NSHXAFÖ 1.8/3 kV (1×1.5 – 1×500 mm²) | Standard 1.8/3 kV halogen-free single-core switchgear and rail vehicle wire (6 kV AC test)
| NSHXAFÖ 3.6/6 kV (1×1.5 – 1×185 mm²) | Medium-voltage 3.6/6 kV halogen-free single-core wire with inner semi-conductive conductor screen
| NSHXAFCMÖ 3.6/6 kV (1×185 mm²) | Screened 3.6/6 kV halogen-free single-core wire with concentric tinned copper wire screen (38.5 mm OD)

## Quality and supply
NSHXAFÖ 1.8/3 kV Halogen-Free Short-Circuit-Proof Single-Core Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxafoe-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-606 / VDE 0250-602. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC spark / dielectric voltage test — 6.0 kV AC (1.8/3 kV series) | Every production length
Routine test | Conductor DC resistance at 20 °C — DIN EN IEC 60228 (VDE 0295) Class 5 | Every production length
Sample test | Halogen-free & acid gas emission test — DIN EN 50267 / IEC 60754 | Per compound batch
Sample test | Smoke density & vertical flame propagation — IEC 61034 · IEC 60332-1-2 | Per production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NSHXAFÖ 1.8/3 kV [1×mm²] · DIN VDE 0250-606 · FRNC / LSZH · CE · [year] · [metre mark]
Supply | Standard packing: Coils or wooden drums; available in 1.8/3 kV, 3.6/6 kV and screened NSHXAFCMÖ
Supply | HS code: 8544.60
Supply | Minimum order: None
Supply | Lead time: None