## Request a quote
Request a quotation for NSHXÖU-O / NSHXÖU-J
Application engineer · VDE mining & industrial rubber cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nshxoeu-flexible-mining-and-industrial-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NSHXÖU-O / NSHXÖU-J NSHXÖU Flexible Mining and Industrial Rubber – Dimensions & weights (22)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxoeu-flexible-mining-and-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| NSHXÖU-O 1×25 | 1×25 | 4 | 11.8 | 12.8 | 240 | 345 | 51 | NSHXÖU-O Single-core power & short-circuit-proof leads (25–240 mm²)
| NSHXÖU-O 1×50 | 1×50 | 1 | 15.2 | 16.5 | 480 | 625 | 66 | NSHXÖU-O Single-core power & short-circuit-proof leads (25–240 mm²)
| NSHXÖU-O 1×95 | 1×95 | 3/0 | 19.7 | 21.4 | 912 | 1135 | 86 | NSHXÖU-O Single-core power & short-circuit-proof leads (25–240 mm²)
| NSHXÖU-O 1×150 | 1×150 | 300 kcmil | 23.9 | 26 | 1440 | 1740 | 104 | NSHXÖU-O Single-core power & short-circuit-proof leads (25–240 mm²)
| NSHXÖU-O 1×240 | 1×240 | 500 kcmil | 29.4 | 32 | 2304 | 2710 | 128 | NSHXÖU-O Single-core power & short-circuit-proof leads (25–240 mm²)
| NSHXÖU-J 3×1.5 | 3G1.5 | 16 | 10.3 | 11.2 | 43 | 175 | 45 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×1.5 | 4G1.5 | 16 | 11.2 | 12.2 | 58 | 215 | 49 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 5×1.5 | 5G1.5 | 16 | 12.3 | 13.4 | 72 | 260 | 54 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 3×2.5 | 3G2.5 | 14 | 11.8 | 12.8 | 72 | 240 | 51 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×2.5 | 4G2.5 | 14 | 12.9 | 14 | 96 | 295 | 56 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 5×2.5 | 5G2.5 | 14 | 14.2 | 15.4 | 120 | 360 | 62 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×4 | 4G4 | 12 | 14.9 | 16.2 | 154 | 420 | 65 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 5×4 | 5G4 | 12 | 16.4 | 17.8 | 192 | 515 | 71 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×6 | 4G6 | 10 | 16.6 | 18 | 230 | 560 | 72 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 5×6 | 5G6 | 10 | 18.4 | 20 | 288 | 690 | 80 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×10 | 4G10 | 8 | 20.6 | 22.4 | 384 | 910 | 90 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×16 | 4G16 | 6 | 23.7 | 25.8 | 614 | 1260 | 103 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×25 | 4G25 | 4 | 28.3 | 30.8 | 960 | 1840 | 123 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×35 | 4G35 | 2 | 31.8 | 34.6 | 1344 | 2410 | 138 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×50 | 4G50 | 1 | 37 | 40.2 | 1920 | 3310 | 161 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×70 | 4G70 | 2/0 | 41.8 | 45.4 | 2688 | 4420 | 182 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
| NSHXÖU-J 4×95 | 4G95 | 3/0 | 46.9 | 51 | 3648 | 5780 | 204 | NSHXÖU-J Multicore heavy-duty mining & industrial cables (3G1.5–4G95)
Dimensions and weights are typical values per DIN VDE 0250-812. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
NSHXÖU-O / NSHXÖU-J NSHXÖU Flexible Mining and Industrial Rubber – Electrical & current ratings (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxoeu-flexible-mining-and-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
1.5 | 16 | 13.7 | 23 | 18
2.5 | 14 | 8.21 | 30 | 25
4 | 12 | 5.09 | 41 | 34
6 | 10 | 3.39 | 53 | 44
10 | 8 | 1.95 | 74 | 61
16 | 6 | 1.24 | 99 | 82
25 | 4 | 0.795 | 131 | 108
35 | 2 | 0.565 | 162 | 135
50 | 1 | 0.393 | 202 | 168
70 | 2/0 | 0.277 | 250 | 207
95 | 3/0 | 0.21 | 301 | 250
150 | 300 kcmil | 0.132 | 404 | 335
240 | 500 kcmil | 0.082 | 540 | 453
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
NSHXÖU-O / NSHXÖU-J NSHXÖU Flexible Mining and Industrial Rubber – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxoeu-flexible-mining-and-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Max. AC 0.7/1.2 kV · DC 0.9/1.8 kV)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −25…+80 °C (Flexing (−40…+80 °C fixed))
Key data | Bending radius | 4–6 × OD (4 × OD fixed · 5–6 × OD flexing)
Key data | Compounds | 3GI3 / HX (EPR core · halogen-free oil sheath)
Key data | Size range | 1.5–240 mm² (1 to 19 cores · Class 5 SnCu)
Electrical | Rated voltage U0/U | 600/1000 V (0.6/1 kV) AC
Electrical | Max. operating voltage AC / DC | 700/1200 V AC · 900/1800 V DC
Electrical | AC test voltage | 3000 V AC (50 Hz, 5 min)
Electrical | Conductor stranding | IEC 60228 / DIN VDE 0295 Class 5 tinned copper
Electrical | Short-circuit-proof rating | Inherently short-circuit & earth-fault proof to 1000 V (VDE 0100-520)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −25 °C to +80 °C
Thermal | Temperature, fixed | −40 °C to +80 °C
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, moving | 5 × OD (≤ 20 mm) · 6 × OD (> 20 mm)
Mechanical | Max. tensile load | 15 N/mm² of total copper cross-section
Mechanical | Mechanical duty class | Extra-heavy mechanical stress (dual-sheath rubber)
Resistance | Halogen-free & acid gas | IEC 60754-1 / EN 60754-2 (pH ≥ 4.3, conductivity ≤ 10 µS/mm)
Resistance | Low smoke emission | IEC 61034-2 / EN 61034-2 light transmittance ≥ 60 %
Resistance | Flame retardance | IEC 60332-1-2 & bunched fire test IEC 60332-3-24 Cat. C
Resistance | Oil & chemical resistance | EN 60811-404 mineral oil resistant (‘Ö’ designation)
Standards | Construction standard | DIN VDE 0250-812
Standards | Selection & installation | DIN VDE 0298-300 & DIN VDE 0298-4
Standards | Conductor standard | IEC 60228 / EN 60228 Class 5
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black (or yellow on request)
Identification | Core identification | Up to 5 cores: HD 308 S2 colour code · ≥ 6 cores: black numbered + GN/YE
Identification | Sheath marking | TEBAOFLEX NSHXÖU [Size] 0.6/1kV DIN VDE 0250-812 HALOGEN-FREE CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
NSHXÖU-O / NSHXÖU-J NSHXÖU Flexible Mining and Industrial Rubber – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxoeu-flexible-mining-and-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned copper conductor | Fine-stranded tinned copper wire (IEC 60228 / DIN VDE 0295 Class 5) | DIN VDE 0295 Class 5
2 | 3GI3 EPR core insulation | Cross-linked ethylene-propylene rubber compound Type 3GI3 (+90 °C rated) | DIN VDE 0207-20 3GI3
3 | Halogen-free inner sheath | Extruded halogen-free elastomeric inner bedding Type GM1b / HM2 filling core interstices
4 | Halogen-free HX outer sheath | Cross-linked halogen-free, flame-retardant and oil-resistant elastomer compound (HX / HM5)
| NSHXÖU-O (Single-Core 1×16–1×240) | Short-circuit-proof single-core power leads without green-yellow earth for switchgear and tunnels
| NSHXÖU-J (Multicore 3G1.5–5G95) | Multi-core power and control cables with green-yellow protective conductor (HD 308 S2 / numbered)
| NSHXÖU-O (Multicore 2×1.5–4×50) | Multi-core power cables without green-yellow earth conductor

## Quality and supply
NSHXÖU-O / NSHXÖU-J NSHXÖU Flexible Mining and Industrial Rubber – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nshxoeu-flexible-mining-and-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 3.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (tinned copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — DIN VDE 0250-812 | Type approval
Standard / approval | DIN VDE 0250-812
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NSHXÖU [Size] 0.6/1 kV DIN VDE 0250-812 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request