## Request a quote
Request a quotation for NSSHÖU
Application engineer · VDE mining & industrial rubber cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NSSHÖU 0.6/1 kV Heavy-Duty Rubber Cable – Sizes & dimensions (92)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Variant & size | Configuration mm² | Cond. Ø mm | Outer Ø min mm | Outer Ø max mm | Weight ≈ kg/km | Min. bend R mm (4×D) | Max. tensile N (15 N/mm²) | Current air A (30 °C) | Series
| NSSHÖU-O 1 × 1.5 mm² | 1 × 1.5 | 1.5 | 6.3 | 7 | 60 | 28 | 23 | 25 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 2.5 mm² | 1 × 2.5 | 1.9 | 7 | 7.7 | 75 | 31 | 38 | 32 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 4 mm² | 1 × 4 | 2.4 | 7.6 | 8.3 | 95 | 34 | 60 | 43 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 6 mm² | 1 × 6 | 2.9 | 8.2 | 8.9 | 120 | 36 | 90 | 56 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 10 mm² | 1 × 10 | 3.8 | 9.5 | 10.2 | 180 | 41 | 150 | 78 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 16 mm² | 1 × 16 | 4.8 | 10.5 | 11.2 | 245 | 45 | 240 | 104 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 25 mm² | 1 × 25 | 6.1 | 13 | 13.7 | 375 | 55 | 375 | 138 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 35 mm² | 1 × 35 | 7.2 | 14.1 | 14.8 | 480 | 60 | 525 | 170 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 50 mm² | 1 × 50 | 8.9 | 16.2 | 16.9 | 660 | 68 | 750 | 212 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 70 mm² | 1 × 70 | 10.6 | 18.3 | 19 | 875 | 76 | 1050 | 263 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 95 mm² | 1 × 95 | 12.5 | 20.5 | 21.7 | 1150 | 87 | 1425 | 316 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 120 mm² | 1 × 120 | 14.2 | 22.8 | 24 | 1430 | 96 | 1800 | 370 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 150 mm² | 1 × 150 | 15.9 | 25 | 26.2 | 1750 | 105 | 2250 | 424 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 185 mm² | 1 × 185 | 17.7 | 28.2 | 29.4 | 2180 | 118 | 2775 | 484 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 240 mm² | 1 × 240 | 20.1 | 31.1 | 32.3 | 2770 | 130 | 3600 | 554 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-O 1 × 300 mm² | 1 × 300 | 22.5 | 34.9 | 36.1 | 3510 | 145 | 4500 | 638 | O/J Single-Core · 1.5–300 mm²
| NSSHÖU-J/-O 3 × 1.5 mm² | 3 × 1.5 | 1.5 | 11.7 | 12.3 | 190 | 50 | 68 | 25 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 2.5 mm² | 3 × 2.5 | 1.9 | 13.1 | 13.7 | 255 | 55 | 113 | 32 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 4 mm² | 3 × 4 | 2.4 | 15.6 | 16.2 | 375 | 65 | 180 | 43 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 6 mm² | 3 × 6 | 2.9 | 16.8 | 17.4 | 465 | 70 | 270 | 56 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 10 mm² | 3 × 10 | 3.8 | 20.2 | 21.3 | 710 | 86 | 450 | 78 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 16 mm² | 3 × 16 | 4.8 | 22.3 | 23.4 | 930 | 94 | 720 | 104 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 25 mm² | 3 × 25 | 6.1 | 26.9 | 28 | 1390 | 112 | 1125 | 138 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 35 mm² | 3 × 35 | 7.2 | 30.2 | 31.4 | 1880 | 126 | 1575 | 170 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 50 mm² | 3 × 50 | 8.9 | 35.8 | 37 | 2500 | 148 | 2250 | 212 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 70 mm² | 3 × 70 | 10.6 | 39.3 | 40.5 | 3460 | 162 | 3150 | 263 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 95 mm² | 3 × 95 | 12.5 | 45.7 | 47.4 | 4570 | 190 | 4275 | 316 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 120 mm² | 3 × 120 | 14.2 | 48.2 | 49.9 | 5220 | 200 | 5400 | 370 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 150 mm² | 3 × 150 | 15.9 | 52.6 | 54.4 | 6460 | 218 | 6750 | 424 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 185 mm² | 3 × 185 | 17.7 | 58.7 | 61 | 7980 | 244 | 8325 | 484 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 1.5 mm² | 4 × 1.5 | 1.5 | 12.5 | 13.1 | 225 | 53 | 90 | 25 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 2.5 mm² | 4 × 2.5 | 1.9 | 15.3 | 15.9 | 350 | 64 | 150 | 32 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 4 mm² | 4 × 4 | 2.4 | 16.7 | 17.3 | 440 | 70 | 240 | 43 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 6 mm² | 4 × 6 | 2.9 | 18.1 | 18.7 | 550 | 75 | 360 | 56 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 10 mm² | 4 × 10 | 3.8 | 21.9 | 23 | 860 | 92 | 600 | 78 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 16 mm² | 4 × 16 | 4.8 | 25.2 | 26.3 | 1210 | 106 | 960 | 104 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 25 mm² | 4 × 25 | 6.1 | 30.6 | 31.8 | 1810 | 128 | 1500 | 138 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 35 mm² | 4 × 35 | 7.2 | 32.8 | 34 | 2330 | 136 | 2100 | 170 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 50 mm² | 4 × 50 | 8.9 | 39 | 40.2 | 3300 | 161 | 3000 | 212 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 70 mm² | 4 × 70 | 10.6 | 42.8 | 44.5 | 4300 | 178 | 4200 | 263 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 95 mm² | 4 × 95 | 12.5 | 49.9 | 51.7 | 5680 | 207 | 5700 | 316 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 120 mm² | 4 × 120 | 14.2 | 55.6 | 57.4 | 6820 | 230 | 7200 | 370 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 150 mm² | 4 × 150 | 15.9 | 60.6 | 62.9 | 8270 | 252 | 9000 | 424 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 4 × 185 mm² | 4 × 185 | 17.7 | 67.4 | 69.7 | 10350 | 279 | 11100 | 484 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 1.5 mm² | 5 × 1.5 | 1.5 | 13.4 | 14 | 270 | 56 | 113 | 25 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 2.5 mm² | 5 × 2.5 | 1.9 | 16.4 | 17 | 410 | 68 | 188 | 32 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 4 mm² | 5 × 4 | 2.4 | 18 | 18.6 | 525 | 75 | 300 | 43 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 6 mm² | 5 × 6 | 2.9 | 20.3 | 21.4 | 715 | 86 | 450 | 56 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 10 mm² | 5 × 10 | 3.8 | 23.7 | 24.8 | 1040 | 100 | 750 | 78 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 16 mm² | 5 × 16 | 4.8 | 27.3 | 28.4 | 1470 | 114 | 1200 | 104 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 5 × 25 mm² | 5 × 25 | 6.1 | 33.2 | 34.4 | 2220 | 138 | 1875 | 138 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 7 × 1.5 mm² | 7 × 1.5 | 1.5 | 16.9 | 17.5 | 400 | 70 | 158 | 16 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 7 × 2.5 mm² | 7 × 2.5 | 1.9 | 19.2 | 19.8 | 560 | 80 | 263 | 21 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 12 × 1.5 mm² | 12 × 1.5 | 1.5 | 19.6 | 20.2 | 540 | 81 | 270 | 12 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 12 × 2.5 mm² | 12 × 2.5 | 1.9 | 22.3 | 23.4 | 790 | 94 | 450 | 16 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 18 × 1.5 mm² | 18 × 1.5 | 1.5 | 22.2 | 23.3 | 750 | 94 | 405 | 11 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 18 × 2.5 mm² | 18 × 2.5 | 1.9 | 26.5 | 27.6 | 1110 | 111 | 675 | 14 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 24 × 1.5 mm² | 24 × 1.5 | 1.5 | 23.7 | 25.1 | 900 | 101 | 540 | 10 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 24 × 2.5 mm² | 24 × 2.5 | 1.9 | 28.4 | 29.6 | 1350 | 119 | 900 | 13 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 50 + 3 × 25/3E mm² | 3 × 50 + 3 × 25/3E | 8.9 | 36.3 | 37.5 | 2790 | 150 | 2250 | 212 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 70 + 3 × 35/3E mm² | 3 × 70 + 3 × 35/3E | 10.6 | 39.7 | 41.4 | 3660 | 166 | 3150 | 263 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 95 + 3 × 50/3E mm² | 3 × 95 + 3 × 50/3E | 12.5 | 46.3 | 48 | 4800 | 192 | 4275 | 316 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 120 + 3 × 70/3E mm² | 3 × 120 + 3 × 70/3E | 14.2 | 48.5 | 50.3 | 5990 | 202 | 5400 | 370 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 150 + 3 × 70/3E mm² | 3 × 150 + 3 × 70/3E | 15.9 | 54.3 | 56.1 | 7030 | 225 | 6750 | 424 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 185 + 3 × 95/3E mm² | 3 × 185 + 3 × 95/3E | 17.7 | 61.7 | 64 | 9030 | 256 | 8325 | 484 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU-J/-O 3 × 240 + 3 × 120/3E mm² | 3 × 240 + 3 × 120/3E | 20.1 | 66.5 | 68.8 | 11280 | 276 | 10800 | 554 | O/J Multicore · 3C–24C & 3+3E
| NSSHÖU 3E 3 × 2.5 + 3 × 2.5/3E mm² | 3 × 2.5 + 3 × 2.5/3E | 1.9 | 16.2 | 16.9 | 370 | 68 | 113 | 32 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 4 + 3 × 4/3E mm² | 3 × 4 + 3 × 4/3E | 2.4 | 17.7 | 18.4 | 490 | 74 | 180 | 43 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 6 + 3 × 6/3E mm² | 3 × 6 + 3 × 6/3E | 2.9 | 18.9 | 19.6 | 590 | 79 | 270 | 56 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 10 + 3 × 10/3E mm² | 3 × 10 + 3 × 10/3E | 3.8 | 22.4 | 23.5 | 890 | 94 | 450 | 78 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 16 + 3 × 16/3E mm² | 3 × 16 + 3 × 16/3E | 4.8 | 26.6 | 27.7 | 1260 | 111 | 720 | 104 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 25 + 3 × 16/3E mm² | 3 × 25 + 3 × 16/3E | 6.1 | 29.9 | 31.1 | 1700 | 125 | 1125 | 138 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 35 + 3 × 16/3E mm² | 3 × 35 + 3 × 16/3E | 7.2 | 33.9 | 35.1 | 2100 | 141 | 1575 | 170 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 50 + 3 × 25/3E mm² | 3 × 50 + 3 × 25/3E | 8.9 | 39.8 | 41.5 | 3060 | 166 | 2250 | 212 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 70 + 3 × 35/3E mm² | 3 × 70 + 3 × 35/3E | 10.6 | 43.4 | 45.1 | 3940 | 181 | 3150 | 263 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 95 + 3 × 50/3E mm² | 3 × 95 + 3 × 50/3E | 12.5 | 50 | 51.8 | 5240 | 208 | 4275 | 316 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 120 + 3 × 70/3E mm² | 3 × 120 + 3 × 70/3E | 14.2 | 54.1 | 55.9 | 6580 | 224 | 5400 | 370 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 150 + 3 × 70/3E mm² | 3 × 150 + 3 × 70/3E | 15.9 | 59.7 | 62 | 7590 | 248 | 6750 | 424 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E 3 × 185 + 3 × 95/3E mm² | 3 × 185 + 3 × 95/3E | 17.7 | 66.1 | 68.4 | 9400 | 274 | 8325 | 484 | 3E Screened · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 2.5 + 3 × 2.5/3E + 3 × 1.5ST mm² | 3 × 2.5 + 3 × 2.5/3E + 3 × 1.5ST | 1.9 | 16.2 | 18.1 | 425 | 73 | 113 | 32 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 4 + 3 × 4/3E + 3 × 1.5ST mm² | 3 × 4 + 3 × 4/3E + 3 × 1.5ST | 2.4 | 17.7 | 19.6 | 540 | 79 | 180 | 43 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 6 + 3 × 6/3E + 3 × 1.5ST mm² | 3 × 6 + 3 × 6/3E + 3 × 1.5ST | 2.9 | 18.9 | 20.3 | 640 | 82 | 270 | 56 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 10 + 3 × 10/3E + 3 × 2.5ST mm² | 3 × 10 + 3 × 10/3E + 3 × 2.5ST | 3.8 | 22.4 | 23.5 | 940 | 94 | 450 | 78 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 16 + 3 × 16/3E + 3 × 2.5ST mm² | 3 × 16 + 3 × 16/3E + 3 × 2.5ST | 4.8 | 26.6 | 27.7 | 1310 | 111 | 720 | 104 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 25 + 3 × 16/3E + 3 × 2.5ST mm² | 3 × 25 + 3 × 16/3E + 3 × 2.5ST | 6.1 | 29.9 | 31.1 | 1800 | 125 | 1125 | 138 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 35 + 3 × 16/3E + 3 × 2.5ST mm² | 3 × 35 + 3 × 16/3E + 3 × 2.5ST | 7.2 | 33.9 | 35.1 | 2230 | 141 | 1575 | 170 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 50 + 3 × 25/3E + 3 × 2.5ST mm² | 3 × 50 + 3 × 25/3E + 3 × 2.5ST | 8.9 | 39.8 | 41.5 | 3160 | 166 | 2250 | 212 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 70 + 3 × 35/3E + 3 × 2.5ST mm² | 3 × 70 + 3 × 35/3E + 3 × 2.5ST | 10.6 | 43.4 | 45.1 | 4210 | 181 | 3150 | 263 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 95 + 3 × 50/3E + 3 × 2.5ST mm² | 3 × 95 + 3 × 50/3E + 3 × 2.5ST | 12.5 | 50 | 51.8 | 5520 | 208 | 4275 | 316 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 120 + 3 × 70/3E + 3 × 2.5ST mm² | 3 × 120 + 3 × 70/3E + 3 × 2.5ST | 14.2 | 54.1 | 55.9 | 6730 | 224 | 5400 | 370 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 150 + 3 × 70/3E + 3 × 2.5ST mm² | 3 × 150 + 3 × 70/3E + 3 × 2.5ST | 15.9 | 59.7 | 62 | 7740 | 248 | 6750 | 424 | 3E+ST Screened + Pilot · 2.5–185 mm²
| NSSHÖU 3E+ST 3 × 185 + 3 × 95/3E + 3 × 2.5ST mm² | 3 × 185 + 3 × 95/3E + 3 × 2.5ST | 17.7 | 66.1 | 68.4 | 9700 | 274 | 8325 | 484 | 3E+ST Screened + Pilot · 2.5–185 mm²
Minimum fixed bending radius rmin is calculated at 4 × OD max (for flexing allow 5 × OD max; for guided deflection allow 10 × OD max per DIN VDE 0298-3).
Maximum dynamic tensile load tmax is 15 N/mm² of total phase-conductor cross-section (for 3+3E and 3E+ST types, calculated on the 3 phase conductors only). Current in free air at 30 °C includes multicore loading conversion factors for 7–24 core control sizes.

## Ampacity, voltage drop & derati
NSSHÖU 0.6/1 kV Heavy-Duty Rubber Cable – Ampacity, voltage drop & derating (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Conductor mm² | Max. DC R 20 °C Ω/km (tinned) | On floor A (30 °C) | Free air A (30 °C) | Reeled 1L A | Reeled 2L A | Reeled 3L A | Voltage drop V/A·km (PF 0.8) | Voltage drop V/A·km (PF 1.0)
1.5 mm² | 13.7 | 24 | 25 | 19 | 15 | 12 | 23.56 | 29.32
2.5 mm² | 8.21 | 30 | 32 | 24 | 18 | 15 | 14.17 | 17.59
4 mm² | 5.09 | 41 | 43 | 33 | 25 | 20 | 8.82 | 10.92
6 mm² | 3.39 | 53 | 56 | 42 | 32 | 26 | 5.9 | 7.27
10 mm² | 1.95 | 74 | 78 | 59 | 45 | 36 | 3.44 | 4.2
16 mm² | 1.24 | 99 | 104 | 79 | 60 | 49 | 2.21 | 2.66
25 mm² | 0.795 | 131 | 138 | 105 | 80 | 64 | 1.45 | 1.71
35 mm² | 0.565 | 162 | 170 | 130 | 99 | 79 | 1.06 | 1.23
50 mm² | 0.393 | 202 | 212 | 162 | 123 | 99 | 0.77 | 0.87
70 mm² | 0.277 | 250 | 263 | 200 | 153 | 123 | 0.56 | 0.61
95 mm² | 0.21 | 301 | 316 | 241 | 184 | 147 | 0.45 | 0.47
120 mm² | 0.164 | 352 | 370 | 282 | 215 | 172 | 0.36 | 0.36
150 mm² | 0.132 | 404 | 424 | 323 | 246 | 198 | 0.31 | 0.29
185 mm² | 0.108 | 461 | 484 | 369 | 281 | 226 | 0.27 | 0.24
240 mm² | 0.0817 | 528 | 554 | 422 | 322 | 259 | 0.22 | 0.18
300 mm² | 0.0654 | 608 | 638 | 486 | 371 | 298
Ambient temperature derating factors (base 30 °C = 1.00, max conductor 90 °C): 10 °C: 1.15 · 15 °C: 1.12 · 20 °C: 1.08 · 25 °C: 1.04 · 30 °C: 1.00 · 35 °C: 0.96 · 40 °C: 0.91 · 45 °C: 0.87 · 50 °C: 0.82 · 55 °C: 0.76 · 60 °C: 0.71 · 65 °C: 0.65 · 70 °C: 0.58 · 75 °C: 0.50 · 80 °C: 0.41.
Multicore loading derating factors (DIN VDE 0298-4): 5 loaded cores: 0.75 · 7 cores: 0.65 · 10 cores: 0.55 · 14 cores: 0.50 · 19 cores: 0.45 · 24 cores: 0.40.

## Technical data
NSSHÖU 0.6/1 kV Heavy-Duty Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U 0.6/1 kV AC · 0.9/1.5 kV DC)
Key data | Configurations | O/J · 3E · 3E+ST (Unscreened, screened & pilot)
Key data | Bending radius | 4–5 × OD (DIN VDE 0298-3 (10 × D guided))
Key data | Temperature | −25…+80 °C (−40…+80 °C fixed installation)
Key data | Conductor max. | +90 °C / 250 °C (continuous / 5 s short-circuit)
Key data | Sizes | 92 (1 × 1.5 to 3 × 240+3 × 120/3E mm²)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (0.9/1.5 kV DC)
Electrical | Max. operating voltage | 0.7/1.2 kV AC · 0.9/1.8 kV DC (DIN VDE 0298-3)
Electrical | AC test voltage | 3.0 kV AC (50 Hz)
Electrical | Current rating | 25 to 638 A in free air at 30 °C (DIN VDE 0298-4)
Electrical | Individual phase screen (3E / 3E+ST) | Tinned Cu braid (≤ 10 mm²) · helical Cu wire screen (≥ 16 mm²)
Thermal | Ambient temperature, flexing | −25 to +80 °C
Thermal | Ambient temperature, fixed | −40 to +80 °C
Thermal | Max. conductor temperature | +90 °C continuous · +250 °C short-circuit
Mechanical | Min. bending radius, fixed | 4 × OD (6 × OD conservative site rule)
Mechanical | Min. bending radius, flexing | 5 × OD free movement (10 × OD guided / reeling)
Mechanical | Max. tensile load | 15 N/mm² mobile operation · 50 N/mm² stationary laying (VDE 0298-3)
Mechanical | Abrasion & tear resistance | Abrasion ≤ 300 mm³ (VDE 0472-605 A) · Tear ≥ 30 N/mm (VDE 0472-613)
Resistance | Oil, chemical & water | Oil resistant (VDE 0472-803 A / EN 60811-404) · Submersible to 100 m
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 (DIN VDE 0472-804 Test B)
Standards | Cable type | DIN VDE 0250-812 · DIN VDE 0250-1 · DIN VDE 0298-3 / -4
Standards | Conductor | IEC 60228 Class 5 / EN 60228 / DIN VDE 0295
Standards | Compounds | 3GI3 EPR (VDE 0207-20) · GM1b/5GM5 inner & 5GM5 outer (VDE 0207-21)
Identification | Core identification | ≤ 5 cores colour-coded (HD 308 / VDE 0293-308); ≥ 6 cores black with white numbers
Identification | Sheath colour | Yellow (black on request)
Identification | Customs tariff (HS) | 8544.49

## Construction
NSSHÖU 0.6/1 kV Heavy-Duty Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible conductor | Electrolytic annealed fine-stranded tinned copper, Class 5 | IEC 60228 Class 5 / EN 60228 / DIN VDE 0295
2 | Separator tape | Polyester separating tape between conductor and EPR insulation where required
3 | Core insulation | Extruded cross-linked ethylene-propylene elastomer (EPR) compound type 3GI3
4 | Individual core screen (3E & 3E+ST only) | Tinned copper braid (≤ 10 mm²) or helical tinned copper wire screen (≥ 16 mm²) over each phase core
5 | Inner sheath | Extruded thermosetting elastomer compound type GM1b or 5GM5 filling interstices
6 | Outer sheath | Heavy-duty cross-linked polychloroprene / synthetic elastomer compound type 5GM5, yellow
| NSSHÖU-O / -J (Unscreened) | Single-core (1 × 1.5–300 mm²) and multicore (3C–24C, plus 3+3E split earth) without (-O) or with (-J) green/yellow PE core
| NSSHÖU 3E (Individually Screened) | 3 phase cores (2.5–185 mm²) each with concentric copper braid/wire screen (3E) for radial earth-fault protection
| NSSHÖU 3E+ST (Screened + Pilot Cores) | 3 individually screened phase cores (2.5–185 mm²) + 3 × 1.5 or 3 × 2.5 mm² insulated control/pilot cores (ST) in outer interstices

## Series
NSSHÖU 0.6/1 kV Heavy-Duty Rubber Cable – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
O/J 1C | NSSHÖU-O Single-Core | 0.6/1 kV | Unscreened · 1C | 16 | High-current single-phase/three-phase feeders, switchgear jumpers and heavy-duty equipment leads
O/J MC | NSSHÖU-J / -O Multicore | 0.6/1 kV | Unscreened · 3C–24C & 3+3E | 50 | Mining, tunnelling, quarry and construction-site power and control connections under high mechanical stress
3E | NSSHÖU 3E Screened | 0.6/1 kV | Cu screen per phase · 3+3E | 13 | Underground and surface mining power feeds requiring individual phase earth-fault screening
3E+ST | NSSHÖU 3E+ST Screened + Pilot | 0.6/1 kV | Cu screen + 3 pilot cores | 13 | Mobile mining cutters, loaders and tunnelling rigs requiring earth-screened phases plus pilot interlock circuits

## Quality and supply
NSSHÖU 0.6/1 kV Heavy-Duty Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nsshoeu-heavy-duty-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-812. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test on completed cable — 3.0 kV AC (50 Hz, 5 min) | Every manufactured length (DIN VDE 0250-812)
Routine test | Conductor DC resistance & spark test — IEC 60228 Class 5 tinned copper limits | Every manufactured length
Sample test | 5GM5 outer sheath abrasion & tear propagation resistance — Abrasion ≤ 300 mm³ (VDE 0472-605 A) · Tear ≥ 30 N/mm (VDE 0472-613) | Per compound batch (DIN VDE 0207-21)
Type test | Oil immersion & vertical flame propagation — EN 60811-404 (VDE 0472-803 A) & IEC/EN 60332-1-2 (VDE 0472-804 B) | Type qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NSSHÖU-J [or -O / 3E / 3E+ST] [size] 0.6/1 kV DIN VDE 0250-812 · [year] · [metre mark]
Supply | Delivery form: 1000 m standard wooden drums or custom cut lengths
Supply | Packaging: Heat-treated seaworthy timber drums with waterproof end caps
Supply | Minimum order: None
Supply | Lead time: None