## Request a quote
Request a quotation for NTMCGCWÖU
Application engineer · MV substation & switchgear cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ntmcgcwoeu-medium-voltage-single-core-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NTMCGCWÖU Flexible MV Single-Core Cable – Dimensions, ampacity & mechanical (38)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcgcwoeu-medium-voltage-single-core-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation · grade | U0/U kV | Phase / Screen mm² | Insulation mm | Sheath mm | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R (fixed) mm | Max. pull N | Current 30 °C A (in air) | Series
| NTMCGCWÖU 1 × 16 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 16 / 16 | 3.4 | 2.2 | 20.3 | 720 | 122 | 240 | 141 | 3.6/6 kV
| NTMCGCWÖU 1 × 25 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 25 / 16 | 3.4 | 2.2 | 21.5 | 828 | 129 | 375 | 187 | 3.6/6 kV
| NTMCGCWÖU 1 × 35 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 35 / 16 | 3.4 | 2.2 | 22.2 | 933 | 133 | 525 | 231 | 3.6/6 kV
| NTMCGCWÖU 1 × 50 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 50 / 16 | 3.4 | 2.2 | 24.2 | 1119 | 145 | 750 | 288 | 3.6/6 kV
| NTMCGCWÖU 1 × 70 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 70 / 16 | 3.4 | 2.5 | 26.6 | 1384 | 160 | 1050 | 357 | 3.6/6 kV
| NTMCGCWÖU 1 × 95 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 95 / 16 | 3.4 | 2.5 | 28.7 | 1637 | 172 | 1425 | 430 | 3.6/6 kV
| NTMCGCWÖU 1 × 120 / 16 mm² · 3.6/6 kV | 3.6/6 | 1 × 120 / 16 | 3.4 | 2.5 | 29.8 | 1888 | 179 | 1800 | 503 | 3.6/6 kV
| NTMCGCWÖU 1 × 150 / 25 mm² · 3.6/6 kV | 3.6/6 | 1 × 150 / 25 | 3.4 | 3 | 32.7 | 2382 | 196 | 2250 | 577 | 3.6/6 kV
| NTMCGCWÖU 1 × 185 / 25 mm² · 3.6/6 kV | 3.6/6 | 1 × 185 / 25 | 3.4 | 3 | 34.9 | 2725 | 209 | 2775 | 658 | 3.6/6 kV
| NTMCGCWÖU 1 × 16 / 16 mm² · 6/10 kV | 6/10 | 1 × 16 / 16 | 3.4 | 2.2 | 21.1 | 755 | 127 | 240 | 141 | 6/10 kV
| NTMCGCWÖU 1 × 25 / 16 mm² · 6/10 kV | 6/10 | 1 × 25 / 16 | 3.4 | 2.2 | 22.3 | 864 | 134 | 375 | 187 | 6/10 kV
| NTMCGCWÖU 1 × 35 / 16 mm² · 6/10 kV | 6/10 | 1 × 35 / 16 | 3.4 | 2.2 | 23 | 970 | 138 | 525 | 231 | 6/10 kV
| NTMCGCWÖU 1 × 50 / 16 mm² · 6/10 kV | 6/10 | 1 × 50 / 16 | 3.4 | 2.5 | 25.6 | 1197 | 154 | 750 | 289 | 6/10 kV
| NTMCGCWÖU 1 × 70 / 16 mm² · 6/10 kV | 6/10 | 1 × 70 / 16 | 3.4 | 2.5 | 27.4 | 1429 | 164 | 1050 | 356 | 6/10 kV
| NTMCGCWÖU 1 × 95 / 16 mm² · 6/10 kV | 6/10 | 1 × 95 / 16 | 3.4 | 2.5 | 29.5 | 1686 | 177 | 1425 | 430 | 6/10 kV
| NTMCGCWÖU 1 × 120 / 16 mm² · 6/10 kV | 6/10 | 1 × 120 / 16 | 3.4 | 3 | 31.6 | 2016 | 190 | 1800 | 503 | 6/10 kV
| NTMCGCWÖU 1 × 150 / 25 mm² · 6/10 kV | 6/10 | 1 × 150 / 25 | 3.4 | 3 | 33.5 | 2438 | 201 | 2250 | 577 | 6/10 kV
| NTMCGCWÖU 1 × 185 / 25 mm² · 6/10 kV | 6/10 | 1 × 185 / 25 | 3.4 | 3.5 | 35.7 | 2785 | 214 | 2775 | 658 | 6/10 kV
| NTMCGCWÖU 1 × 240 / 25 mm² · 6/10 kV | 6/10 | 1 × 240 / 25 | 3.4 | 3.5 | 41.6 | 3460 | 250 | 3600 |  | 6/10 kV
| NTMCGCWÖU 1 × 16 / 16 mm² · 12/20 kV | 12/20 | 1 × 16 / 16 | 5.5 | 2.5 | 25.9 | 994 | 155 | 240 | 150 | 12/20 kV
| NTMCGCWÖU 1 × 25 / 16 mm² · 12/20 kV | 12/20 | 1 × 25 / 16 | 5.5 | 2.5 | 27.1 | 1116 | 163 | 375 | 198 | 12/20 kV
| NTMCGCWÖU 1 × 35 / 16 mm² · 12/20 kV | 12/20 | 1 × 35 / 16 | 5.5 | 2.5 | 27.8 | 1230 | 167 | 525 | 245 | 12/20 kV
| NTMCGCWÖU 1 × 50 / 16 mm² · 12/20 kV | 12/20 | 1 × 50 / 16 | 5.5 | 2.5 | 29.8 | 1440 | 179 | 750 | 307 | 12/20 kV
| NTMCGCWÖU 1 × 70 / 16 mm² · 12/20 kV | 12/20 | 1 × 70 / 16 | 5.5 | 3 | 32.6 | 1767 | 196 | 1050 | 379 | 12/20 kV
| NTMCGCWÖU 1 × 95 / 16 mm² · 12/20 kV | 12/20 | 1 × 95 / 16 | 5.5 | 3 | 34.7 | 2048 | 208 | 1425 | 456 | 12/20 kV
| NTMCGCWÖU 1 × 120 / 16 mm² · 12/20 kV | 12/20 | 1 × 120 / 16 | 5.5 | 3 | 35.8 | 2312 | 215 | 1800 | 531 | 12/20 kV
| NTMCGCWÖU 1 × 150 / 25 mm² · 12/20 kV | 12/20 | 1 × 150 / 25 | 5.5 | 3.5 | 38.7 | 2846 | 232 | 2250 | 611 | 12/20 kV
| NTMCGCWÖU 1 × 185 / 25 mm² · 12/20 kV | 12/20 | 1 × 185 / 25 | 5.5 | 3.5 | 40.9 | 3218 | 245 | 2775 | 698 | 12/20 kV
| NTMCGCWÖU 1 × 16 / 16 mm² · 18/30 kV | 18/30 | 1 × 16 / 16 | 8 | 3 | 31.9 | 1368 | 191 | 240 | 150 | 18/30 kV
| NTMCGCWÖU 1 × 25 / 16 mm² · 18/30 kV | 18/30 | 1 × 25 / 16 | 8 | 3 | 33.1 | 1505 | 199 | 375 | 198 | 18/30 kV
| NTMCGCWÖU 1 × 35 / 16 mm² · 18/30 kV | 18/30 | 1 × 35 / 16 | 8 | 3 | 33.8 | 1629 | 203 | 525 | 245 | 18/30 kV
| NTMCGCWÖU 1 × 50 / 16 mm² · 18/30 kV | 18/30 | 1 × 50 / 16 | 8 | 3 | 35.8 | 1866 | 215 | 750 | 307 | 18/30 kV
| NTMCGCWÖU 1 × 70 / 16 mm² · 18/30 kV | 18/30 | 1 × 70 / 16 | 8 | 3.5 | 38.6 | 2230 | 232 | 1050 | 379 | 18/30 kV
| NTMCGCWÖU 1 × 95 / 16 mm² · 18/30 kV | 18/30 | 1 × 95 / 16 | 8 | 3.5 | 40.7 | 2539 | 244 | 1425 | 456 | 18/30 kV
| NTMCGCWÖU 1 × 120 / 16 mm² · 18/30 kV | 18/30 | 1 × 120 / 16 | 8 | 3.5 | 41.8 | 2818 | 251 | 1800 | 531 | 18/30 kV
| NTMCGCWÖU 1 × 150 / 25 mm² · 18/30 kV | 18/30 | 1 × 150 / 25 | 8 | 3.5 | 43.7 | 3284 | 262 | 2250 | 611 | 18/30 kV
| NTMCGCWÖU 1 × 185 / 25 mm² · 18/30 kV | 18/30 | 1 × 185 / 25 | 8 | 3.5 | 45.9 | 3680 | 275 | 2775 | 698 | 18/30 kV
| NTMCGCWÖU 1 × 240 / 25 mm² · 18/30 kV | 18/30 | 1 × 240 / 25 | 8 | 3.5 | 51.8 | 4485 | 311 | 3600 |  | 18/30 kV
Current ratings in air at 30 °C ambient (DIN VDE 0298-4). For a three-phase circuit using three single-core cables, apply grouping and trefoil/flat spacing factors per DIN VDE 0298-4.

## Technical data
NTMCGCWÖU Flexible MV Single-Core Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcgcwoeu-medium-voltage-single-core-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6–18/30 kV (U0/U · 4 voltage grades)
Key data | Construction | 1C + Cu screen (16 or 25 mm² concentric screen)
Key data | Bending radius | 6–10 × OD (6 × OD fixed · 10 × OD flexing)
Key data | Temperature | −25…+60 °C (mobile; −40…+80 °C fixed)
Key data | Conductor max. | +90 °C / 250 °C (continuous / short-circuit (3GI3 EPR))
Key data | Sizes | 38 (1 × 16/16 to 1 × 240/25 mm²)
Electrical | Rated voltage U0/U | 3.6/6, 6/10, 12/20, 18/30 kV (8.7/15 kV on request)
Electrical | Max. operating voltage AC | 4.2/7.2 · 6.9/12 · 13.9/24 · 20.8/36 kV
Electrical | AC test voltage | 11 kV (3.6/6) · 17 kV (6/10) · 29 kV (12/20) · 43 kV (18/30)
Electrical | Concentric screen | 16 mm² (up to 120 mm²) · 25 mm² (150–240 mm²) tinned Cu
Electrical | Current rating | 141 to 698 A at 30 °C in air (DIN VDE 0298-4)
Thermal | Ambient temperature, flexing | −25 to +60 °C (conductor +90 °C)
Thermal | Ambient temperature, fixed | −40 to +80 °C (conductor +90 °C)
Thermal | Max. conductor temperature | +90 °C continuous · +250 °C short-circuit
Mechanical | Min. bending radius, fixed | 6 × OD
Mechanical | Min. bending radius, flexing | 10 × OD (12 × OD forced guidance)
Mechanical | Max. tensile load | 15 N/mm² of copper conductor cross-section
Resistance | Oil, UV & ozone | Oil, UV, sunlight, ozone and moisture resistant
Resistance | Flame retardance | Flame retardant (IEC 60332-1-2)
Standards | Cable type | DIN VDE 0250-813
Standards | Conductor | IEC 60228 Class 5 / HD 383 / DIN VDE 0295
Standards | Compounds | 3GI3 EPR (VDE 0207-20) · 5GM3/5GM5 sheath (VDE 0207-21)
Identification | Sheath colour | Red (other colours on request)
Identification | Size notation | 1 × phase conductor / concentric screen mm² (e.g. 1×150/25)
Identification | Customs tariff (HS) | 8544.60

## Construction
NTMCGCWÖU Flexible MV Single-Core Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcgcwoeu-medium-voltage-single-core-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductor | Annealed flexible stranded tinned copper, Class 5 | IEC 60228 Class 5 / HD 383 / DIN VDE 0295
2 | Inner conductor screen | Semi-conductive tape + extruded semi-conductive rubber layer
3 | Core insulation | Ethylene-propylene rubber (EPR) compound type 3GI3
4 | Outer insulation screen | Extruded semi-conductive rubber layer over the 3GI3 insulation | DIN VDE 0250-813 radial field control
5 | Concentric copper screen | Helical warp or braid of tinned copper wires (16 mm² or 25 mm²)
6 | Separator tape | Synthetic non-woven separating tape wrap over copper screen
7 | Outer sheath | Heavy-duty thermosetting elastomer compound type 5GM3 or 5GM5, red
| 1 × 16/16 to 1 × 120/16 | Single phase conductor (16–120 mm²) with 16 mm² concentric tinned-copper screen
| 1 × 150/25 to 1 × 240/25 | Single phase conductor (150–240 mm²) with 25 mm² concentric tinned-copper screen

## Quality and supply
NTMCGCWÖU Flexible MV Single-Core Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcgcwoeu-medium-voltage-single-core-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage test between conductor and concentric screen — 11 kV (3.6/6) · 17 kV (6/10) · 29 kV (12/20) · 43 kV (18/30) | Every manufactured length (DIN VDE 0250-813)
Routine test | Conductor & concentric screen DC resistance — IEC 60228 Class 5 | Every length
Sample test | 3GI3 insulation & 5GM3 sheath mechanical & oil ageing — DIN VDE 0207-20 & 0207-21 | Per compound batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (N)TMCGCWÖU 1x95/16 6/10 kV DIN VDE 0250-813 · [year] · [metre mark]
Supply | Delivery form: 1000 m standard drums or custom cut-to-length phase sets
Supply | Packaging: Heat-treated timber export drums, lagged and end-sealed
Supply | Minimum order: None
Supply | Lead time: None