## Request a quote
Request a quotation for NTMCWÖU
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ntmcwoeu-extra-flexible-single-core-mv-connection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NTMCWÖU Extra-Flexible Single-Core MV Connection Cable – 6/10 kV & 12/20 kV dimensions & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcwoeu-extra-flexible-single-core-mv-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | VDE designation | Conductor & voltage | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Air 30°C A | Series
| NTMCWÖU 1×35 6/10kV | 1 × 35 mm² Cl.5 Tinned Cu · 6/10 kV | 19.8 | 580 | 0.565 | 198 | 6/10 kV NTMCWÖU Unscreened
| NTMCWÖU 1×70 6/10kV | 1 × 70 mm² Cl.5 Tinned Cu · 6/10 kV | 23.6 | 965 | 0.277 | 305 | 6/10 kV NTMCWÖU Unscreened
| NTMCWÖU 1×120 6/10kV | 1 × 120 mm² Cl.5 Tinned Cu · 6/10 kV | 27.8 | 1490 | 0.164 | 430 | 6/10 kV NTMCWÖU Unscreened
| NTMCWÖU 1×240 6/10kV | 1 × 240 mm² Cl.5 Tinned Cu · 6/10 kV | 35.2 | 2760 | 0.0817 | 680 | 6/10 kV NTMCWÖU Unscreened
| (N)TMCWÖU 1×50 12/20kV | 1 × 50 mm² Cl.5 Tinned Cu · 12/20 kV | 25.4 | 890 | 0.393 | 248 | 12/20 kV (N)TMCWÖU Unscreened
| (N)TMCWÖU 1×150 12/20kV | 1 × 150 mm² Cl.5 Tinned Cu · 12/20 kV | 33.4 | 1950 | 0.132 | 500 | 12/20 kV (N)TMCWÖU Unscreened
Also stocked in 3.6/6 kV and 18/30 kV (and 26/45 kV railway pantograph version) from 16 mm² to 500 mm².

## Technical data
NTMCWÖU Extra-Flexible Single-Core MV Connection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcwoeu-extra-flexible-single-core-mv-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | DIN VDE 0250-813 (Single-core flexible MV rubber)
Key data | Voltage classes | 3.6/6 to 18/30 k (3.6/6, 6/10, 12/20 & 18/30 kV)
Key data | Cross-sections | 1 × 16 to 500 mm (Class 5 fine tinned Cu)
Key data | Stress control | Inner Semicon (' (Unscreened outer (fast lugging))
Key data | Insulation | 3GI3 EPR (+90 °C (Ozone & corona resistant)
Key data | Outer sheath | 5GM3 PCP ('WÖU') (Weather, oil & flame resistant)
Electrical | Rated voltage tiers (Uo/U) | 3.6/6 kV · 6/10 kV · 12/20 kV · 18/30 kV (Umax 7.2 / 12 / 24 / 36 kV)
Electrical | Routine AC test voltage | 11 kV (3.6/6) · 17 kV (6/10) · 29 kV (12/20) · 43 kV (18/30) for 5 min
Electrical | Max. DC resistance @ 20 °C | 0.798 Ω/km (25) · 0.393 Ω/km (50) · 0.206 Ω/km (95) · 0.0817 Ω/km (240)
Electrical | Free-air ampacity (30 °C) | 158 A (25) · 245 A (50) · 375 A (95) · 500 A (150) · 680 A (240)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C (up to 5 s)
Thermal | Ambient temperature range | -40 °C to +80 °C (fixed) · -25 °C to +80 °C (flexible)
Mechanical | Min. bend radius | 5 × OD (fixed cubicle routing) · 10 × OD (flexible movement)
Mechanical | Max. tensile load | 15 N / mm² of copper conductor cross-section
Mechanical | Termination clearance | No outer screen strip-back needed; compact lug termination
Resistance | Ozone & corona resistance | 3GI3 EPR + 5GM3 PCP resists high-voltage surface ozone in air
Resistance | Oil & chemical resistance | EN 60811-404 mineral & transformer oil resistant ('Ö')
Resistance | Flame propagation | IEC 60332-1-2 / DIN EN 60332-1-2 self-extinguishing ('U')
Standards | Design standard | DIN VDE 0250-813 (NTMCWÖU)
Standards | Installation & ampacity | DIN VDE 0298-3 & DIN VDE 0298-4
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | VDE code breakdown | N=VDE std · TM=MV flex · C=Inner semicon · W=Weather · Ö=Oil · U=Flame
Identification | Outer sheath colour | Black or Red
Identification | Customs tariff (HS) | 8544.6010

## Construction
NTMCWÖU Extra-Flexible Single-Core MV Connection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcwoeu-extra-flexible-single-core-mv-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 fine-stranded tinned copper conductor | Electrolytic tin-coated annealed flexible copper wires per IEC 60228 / DIN VDE 0295 Class 5 (16 mm² to 500 mm²)
2 | Extruded inner semiconducting elastomer layer ('C') | Vulcanized semiconducting rubber layer bonded over the stranded conductor
3 | 3GI3 Ethylene Propylene Rubber (EPR) MV dielectric | 90 °C ozone-, corona- and heat-resistant thermoset EPR compound Type 3GI3 per DIN VDE 0207-20
4 | 5GM3 Polychloroprene ('WÖU') weather & oil-resistant sheath | Heavy-duty cross-linked polychloroprene rubber compound Type 5GM3 per DIN VDE 0207-21 in Black or Red
| NTMCWÖU 3.6/6 kV & 6/10 kV (1×16 to 1×500 mm²) | Unscreened flexible MV jumper cable for 3.3 kV, 6.6 kV and 10/11 kV motor terminal boxes and switchgear cells
| (N)TMCWÖU 12/20 kV & 18/30 kV (1×25 to 1×500 mm²) | Unscreened flexible MV connection cable for 15 kV, 20 kV and 30 kV transformer cubicles and dry-type coil leads

## Quality and supply
NTMCWÖU Extra-Flexible Single-Core MV Connection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntmcwoeu-extra-flexible-single-core-mv-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % High-voltage AC water-bath dielectric test (11–43 kV for 5 min) — Zero breakdown across entire 3GI3 EPR + 5GM3 rubber wall | Every manufactured drum
Type test | DIN VDE 0207-20 high-concentration ozone & corona endurance test — Zero surface ozone cracking when bent around mandrel under HV stress | Type qualification
Sample test | 5GM3 polychloroprene hot-oil immersion, tensile & IEC 60332-1-2 flame — Meets DIN VDE 0207-21 mechanical and oil retention limits | Per production batch
Standard / approval | DIN VDE 0250-813 (NTMCWÖU)
Standard / approval | DIN VDE 0298-3 / 0298-4
Standard / approval | RoHS 2, REACH & CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NTMCWÖU 6/10kV DIN VDE 0250-813 CE
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP