## Request a quote
Request a quotation for NTSCGECCWÖU
Share your operating voltage, core configuration, and trailing/handler conditions for NTSCGECCWÖU.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ntscgeccwoeu-steel-wire-armoured-mv-trailing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
NTSCGECCWÖU Steel-Wire Armoured MV Trailing Cable – Dimensions & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntscgeccwoeu-steel-wire-armoured-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| NTSCGECCWÖU 3×25+25CW 3.6/6 kV | 3×25 + 25CW (3.6/6 kV) | 25 | 45 | 1120 | 3180 | 270 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×35+25CW 3.6/6 kV | 3×35 + 25CW (3.6/6 kV) | 35 | 48.2 | 1410 | 3690 | 289 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×50+25CW 3.6/6 kV | 3×50 + 25CW (3.6/6 kV) | 50 | 52.5 | 1850 | 4480 | 315 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×70+35CW 3.6/6 kV | 3×70 + 35CW (3.6/6 kV) | 70 | 57.2 | 2530 | 5490 | 343 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×95+50CW 3.6/6 kV | 3×95 + 50CW (3.6/6 kV) | 95 | 62.5 | 3450 | 6810 | 375 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×120+70CW 3.6/6 kV | 3×120 + 70CW (3.6/6 kV) | 120 | 67.2 | 4390 | 8150 | 403 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×35+25CW 6/10 kV | 3×35 + 25CW (6/10 kV) | 35 | 51.5 | 1445 | 4120 | 309 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×50+25CW 6/10 kV | 3×50 + 25CW (6/10 kV) | 50 | 55.8 | 1885 | 4940 | 335 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×70+35CW 6/10 kV | 3×70 + 35CW (6/10 kV) | 70 | 60.5 | 2570 | 6010 | 363 | Standard NTSCGECCWÖU configurations
| NTSCGECCWÖU 3×50+25CW 12/20 kV | 3×50 + 25CW (12/20 kV) | 50 | 63 | 1950 | 6120 | 378 | Standard NTSCGECCWÖU configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per DIN VDE 0250-813.

## Electrical & ampacity data
NTSCGECCWÖU Steel-Wire Armoured MV Trailing Cable – Electrical & ampacity data (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntscgeccwoeu-steel-wire-armoured-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
3×25 + 25CW (3.6/6 kV) | 0.799 | 122 | 104 | 151 | 11000
3×35 + 25CW (3.6/6 kV) | 0.568 | 150 | 128 | 168 | 11000
3×50 + 25CW (3.6/6 kV) | 0.396 | 187 | 159 | 192 | 11000
3×70 + 35CW (3.6/6 kV) | 0.279 | 229 | 195 | 226 | 11000
3×95 + 50CW (3.6/6 kV) | 0.211 | 276 | 235 | 267 | 11000
3×120 + 70CW (3.6/6 kV) | 0.165 | 319 | 271 | 308 | 11000
3×35 + 25CW (6/10 kV) | 0.568 | 150 | 128 | 168 | 17000
3×50 + 25CW (6/10 kV) | 0.396 | 187 | 159 | 192 | 17000
3×70 + 35CW (6/10 kV) | 0.279 | 229 | 195 | 226 | 17000
3×50 + 25CW (12/20 kV) | 0.396 | 187 | 159 | 192 | 30000
Current ratings apply at +30 °C ambient in free air; apply standard derating factors for elevated ambient or drum layers.

## Technical data
NTSCGECCWÖU Steel-Wire Armoured MV Trailing Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntscgeccwoeu-steel-wire-armoured-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6–12/20 kV (Umax 7.2 kV / 12 kV / 24 kV)
Key data | Screen & armour | CGE + CCW (Core screen + wave Cu/steel armour)
Key data | Conductor | Class 5 Tinned (DIN EN 60228 tinned copper)
Key data | Insulation | 3GI3 MV EPR (Triple-extruded +90 °C EPR)
Key data | Outer sheath | 5GM5 PCP (Heavy-duty flame/oil rubber)
Key data | Min. bend radius | 8×D / 12×D (Fixed 8×D · trailing 12×D)
Electrical | Rated voltage U0/U | 3.6/6 kV · 6/10 kV · 12/20 kV
Electrical | AC routine test voltage | 11 kV (3.6/6 kV) · 17 kV (6/10 kV) · 29 kV
Electrical | Partial discharge level | ≤ 20 pC at 2 U0
Electrical | Dual metallic screening | Individual phase screen (C) + overall wave
Thermal | Max. conductor operating temp. | +90 °C
Thermal | Max. short-circuit temperature | +250 °C (5 s)
Thermal | Ambient temperature (trailing) | -25 °C to +60 °C
Thermal | Ambient temperature (fixed) | -40 °C to +80 °C
Mechanical | Armour system | Wave-laid galvanized steel + copper wires
Mechanical | Min. bending radius (fixed | 8 × D fixed · 12 × D trailing
Mechanical | Max. tensile load | 20 N/mm² of copper cross-section
Resistance | Oil & chemical resistance | DIN EN 60811-404 (5GM5 compound)
Resistance | Flame retardancy | DIN EN 60332-1-2 self-extinguishing
Resistance | Weather & UV resistance | Suitable for permanent outdoor open-cast
Standards | Primary specification | DIN VDE 0250-813
Standards | Conductor standard | DIN EN 60228 Class 5 tinned copper
Standards | Compound standard | DIN VDE 0207-20 (3GI3) & 0207-21 (5GM5)
Identification | Core identification | Numbered phase cores 1, 2, 3 +
Identification | Outer sheath colour | Red or Yellow with vulcanised legend

## Construction
NTSCGECCWÖU Steel-Wire Armoured MV Trailing Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntscgeccwoeu-steel-wire-armoured-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductors | Finely stranded tinned copper, Class 5 per DIN EN 60228 | DIN EN 60228 Class 5
2 | Inner & outer semicon (GE) | Triple-extruded semi-conductive elastomeric stress control layers | DIN VDE 0250-813
3 | MV EPR insulation (3GI3) | Cross-linked ethylene propylene rubber compound 3GI3 | DIN VDE 0207-20
4 | Individual phase screen (C) | Tinned copper wire/braid screen over each phase core | DIN VDE 0250-813
5 | Inner sheath | Heavy-duty elastomer inner sheath compound GM1b / 5GM3 | DIN VDE 0250-813
6 | Wave-laid Cu/steel armour (CW) | Corrugated wave-laid galvanized steel and tinned copper wires with counter-tape | DIN VDE 0250-813
7 | Outer sheath (5GM5) | Extra-heavy flame-retardant, oil- and tear-resistant polychloroprene 5GM5 | DIN VDE 0207-21
| NTSCGECCWÖU 3.6/6 kV | 3.6/6 kV (Umax 7.2 kV) double-screened & CW armoured MV trailing cable.
| NTSCGECCWÖU 6/10 kV & 12/20 kV | 6/10 kV and 12/20 kV MV trailing feeder for open-pit and deep mine distribution.

## Quality and supply
NTSCGECCWÖU Steel-Wire Armoured MV Trailing Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ntscgeccwoeu-steel-wire-armoured-mv-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | MV AC voltage withstand — 11 kV (3.6/6 kV), 17 kV (6/10 kV), or 29 kV (12/20 kV) / 5 min | 100 % of drums
Routine test | Partial discharge test — ≤ 20 pC at 2 U0 per DIN VDE 0250-813 | 100 % of drums
Sample test | CCW armour impact & bend test — DIN VDE 0250-813 mechanical compliance | Per production batch
Type test | Flame & oil resistance — DIN EN 60332-1-2 & EN 60811-404 | Type approval
Standard / approval | DIN VDE 0250-813
Standard / approval | DIN EN 60332-1-2
Standard / approval | EN 10204 3.1
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NTSCGECCWÖU 3.6/6–12/20 kV VDE
Supply | Delivery form: Fumigated export wooden drums
Supply | Standard drum lengths: 300 m · 500 m · 1000 m (or custom cut
Supply | MOQ: 100 m (stock sizes) · 300 m (custom build)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP