## Request a quote
Request a quotation for NTSWÖU-J / NTSWÖU 0.6/1 kV Tunnel & E-Loader Cable
Application engineer · Underground mining & tunnel cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/n-tswoeu-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
(N)TSWÖU / NTSWÖU-J 0.6/1 kV Tunnel & Mining Cable – NTSWÖU-J & E-Loader Series (0.6/1 kV) (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tswoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation DIN VDE 0250-813 | Construction Variant | Phase mm² | Earth / Armour & Pilots | Min. OD mm | Max. OD mm | Mass ≈ kg/km | Tensile 15N/mm² N | Current 30°C A (VDE 0298-4)
| NTSWÖU-J · 3×25 + 3×25/3 | NTSWÖU-J (Cl. 5) | 25 | 3×25/3 | 40 | 44 | 2470 | 1125 | 131
| NTSWÖU-J · 3×35 + 3×25/3 | NTSWÖU-J (Cl. 5) | 35 | 3×25/3 | 44.4 | 48.4 | 3150 | 1575 | 162
| NTSWÖU-J · 3×50 + 3×25/3 | NTSWÖU-J (Cl. 5) | 50 | 3×25/3 | 47.7 | 51.7 | 3750 | 2250 | 202
| NTSWÖU-J · 3×70 + 3×35/3 | NTSWÖU-J (Cl. 5) | 70 | 3×35/3 | 52.3 | 56.3 | 4690 | 3150 | 250
| NTSWÖU-J · 3×95 + 3×50/3 | NTSWÖU-J (Cl. 5) | 95 | 3×50/3 | 59.9 | 63.9 | 6210 | 4275 | 301
| NTSWÖU-J · 3×120 + 3×70/3 | NTSWÖU-J (Cl. 5) | 120 | 3×70/3 | 63.8 | 67.8 | 7430 | 5400 | 352
| NTSWÖU-J · 3×150 + 3×70/3 | NTSWÖU-J (Cl. 5) | 150 | 3×70/3 | 69.2 | 73.2 | 8900 | 6750 | 404
| NTSWÖU-J · 3×185 + 3×95/3 | NTSWÖU-J (Cl. 5) | 185 | 3×95/3 | 73.1 | 77.1 | 10330 | 8325 | 461
| NTSWÖU E-Loader · 3×50/25KON+3×ST | E-Loader (Cl. 6 + KON) | 50 | 25KON + 3×ST | 54 | 56 | 4950 | 2250 | 202
On NTSWÖU E-Loader 3×50/25KON + 3×ST: insulation thickness is 2.0 mm, GM1b inner sheath thickness is 3.0 mm, 5GM5 outer sheath thickness is 5.0 mm, and nominal overall diameter is 56 mm (4,950 kg/km).
Current ratings are based on DIN VDE 0298-4 at 30 °C ambient temperature; standard drum packing length is 500 m.

## Technical data
(N)TSWÖU / NTSWÖU-J 0.6/1 kV Tunnel & Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tswoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (3 kV) (DIN VDE 0250-813)
Key data | Core arrangement | 3P+3E or KON+3ST (Split PE or 25KON braid)
Key data | Phase size range | 25–185 mm² (8 trailing + E-Loader)
Key data | Sheath system | GM1b + 5GM5 (Yellow or black 5GM5)
Key data | Operating temp. | −25 to +90 °C (Fixed −40 to +90 °C)
Key data | Conductor class | Class 5 / Cl. 6 (Cl. 6 on E-Loader build)
Electrical | Rated & test voltage | U0/U 0.6/1 kV AC · Routine dielectric test voltage 3 kV AC
Electrical | Current carrying capacity | 131 A (25 mm²) to 461 A (185 mm²) according to DIN VDE 0298-4 (30 °C ambient)
Electrical | Protective earth & pilot options | NTSWÖU-J: 3 split interstitial earth cores (25/3 to 95/3) · E-Loader: 25 mm² Cu/steel braided concentric earth (25KON) + 3 pilot cores (3×ST)
Thermal | Conductor temperature | +90 °C maximum continuous operating temperature · +250 °C short-circuit temperature
Thermal | Ambient temperature range | Fixed installation −40 °C to +90 °C · Mobile / trailing operation −25 °C to +90 °C
Mechanical | Min. bending radius | According to DIN VDE 0298-3 Table 3 (4 × D fixed installation · 5 × D to 10 × D mobile/reeling)
Mechanical | E-Loader extreme mechanical reinforcement | Combined copper-steel braided concentric armour (25KON) over GM1b inner sheath resists LHD guide-pulley impact, crushing and high tensile loads
Resistance | Flame & oil resistance | Flame retardant to DIN EN 60332-1-2 / VDE 0482-332-1-2 · Oil resistant to HD/EN/IEC 60811-2-1
Resistance | Abrasion, tear & wet-heading durability | Dual elastomer sheath (GM1b inner + 5GM5 outer) for dry, damp and flooded underground mines and tunnels
Standards | Applicable VDE standards | DIN VDE 0250-813 · DIN VDE 0250-1 · DIN VDE 0207-20 (3GI3) · DIN VDE 0207-21 (GM1b / 5GM5)
Standards | Conductor stranding classes | DIN VDE 0295 Class 5 tinned copper (NTSWÖU-J series) · DIN VDE 0295 Class 6 extra-finely stranded tinned copper (E-Loader series)
Identification | Outer jacket colour | High-visibility Yellow or Black Type 5GM5 polychloroprene outer sheath
Identification | Series variants | NTSWÖU-J Tunnel Trailing Series (3×25 to 3×185 mm² with split earths) · NTSWÖU E-Loader Series (3×50/25KON + 3×ST)

## Construction
(N)TSWÖU / NTSWÖU-J 0.6/1 kV Tunnel & Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tswoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductor | Electrolytic stranded tinned copper wire, DIN VDE 0295 Class 5 (NTSWÖU-J) or Class 6 extra-flexible (E-Loader) | DIN VDE 0295
2 | Core insulation | EPR rubber compound Type 3GI3 (2.0 mm nominal wall on 3×50 E-Loader) | DIN VDE 0207-20
3 | Interstitial earth / pilot cores | Three split protective earth cores (25/3 to 95/3 on NTSWÖU-J) or 3 special Cu/steel-braided pilot cores (3×ST on E-Loader) | DIN VDE 0250-813
4 | Inner sheath | Special elastomeric rubber compound Type GM1b (3.0 mm wall on E-Loader) | DIN VDE 0207-21
5 | Concentric Cu/steel braided earth (E-Loader) | Combined copper and galvanised steel wire braided armour/earth conductor (25KON on E-Loader build) | DIN VDE 0250-813
6 | Outer sheath | Heavy-duty chlorinated elastomer Type 5GM5 (5.0 mm wall on E-Loader), yellow or black, oil and flame resistant | DIN VDE 0207-21
| NTSWÖU-J Tunnel Trailing Series (25–185 mm²) | Class 5 tinned Cu · 3×25+3×25/3 to 3×185+3×95/3 mm² · GM1b inner + yellow/black 5GM5 outer sheath · 40.0–77.1 mm OD
| NTSWÖU E-Loader Reeling Build (3×50/25KON + 3×ST) | Class 6 extra-flexible tinned Cu · 2.0 mm EPR + 3.0 mm GM1b + 25KON Cu/steel braid + 5.0 mm yellow 5GM5 sheath · 56 mm OD

## Quality and supply
(N)TSWÖU / NTSWÖU-J 0.6/1 kV Tunnel & Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/n-tswoeu-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-813 · DIN VDE 0298-3 / 0298-4. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3 kV AC dielectric withstand test — 3.0 kV AC applied to 0.6/1 kV 3GI3 EPR insulated cores per DIN VDE 0250-813 and DIN VDE 0472-508 | Every shipping drum
Routine test | Conductor, split earth & 25KON armour DC resistance — Verified on Class 5 / Class 6 tinned copper phase conductors and earth/pilot elements per DIN VDE 0472-501 | Every shipping drum
Sample test | DIN EN 60332-1-2 flame & EN 60811-2-1 oil resistance — Flame propagation and hot oil immersion verified on Type 5GM5 heavy-duty elastomer outer sheath | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · NTSWÖU-J 0.6/1 kV · VDE 0250-813
Supply | Delivery form: 500 m standard wooden drums or custom reeling lengths on request
Supply | Lengths: 500 m standard or custom cut lengths per tunnel/loader schedule
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None