## Request a quote
Request a quotation for NYM-J
Application engineer · LV/MV/HV power distribution
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nym-j-nym-o-pvc-building-installation-sheathed-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
NYM-J / NYM-O 300/500 V PVC Building & Damp-Location Fixed – Dimensions, construction & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nym-j-nym-o-pvc-building-installation-sheathed-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0250-204. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| NYM-J 3G1.5 | 3 × 1.5 mm² | 8.4 | 105 | 68 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G1.5 | 4 × 1.5 mm² | 9.2 | 128 | 74 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 5G1.5 | 5 × 1.5 mm² | 10.1 | 156 | 81 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 3G2.5 | 3 × 2.5 mm² | 9.8 | 148 | 78 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G2.5 | 4 × 2.5 mm² | 10.8 | 186 | 86 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 5G2.5 | 5 × 2.5 mm² | 11.9 | 228 | 95 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G4 | 4 × 4.0 mm² | 12.6 | 268 | 101 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G6 | 4 × 6.0 mm² | 14.2 | 365 | 114 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G10 | 4 × 10 mm² | 17.5 | 580 | 140 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G16 | 4 × 16 mm² | 20.4 | 845 | 163 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G25 | 4 × 25 mm² | 24.8 | 1290 | 198 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
| NYM-J 4G35 | 4 × 35 mm² | 27.9 | 1710 | 223 | NYM-J Standard Production Schedule (300/500 V · −40…+70 °C)
Single-core and multi-core sizes from 0.5 mm² up to 630 mm² (or AWG/kcmil) available per DIN VDE 0250-204.

## Conductor resistance & current-
NYM-J / NYM-O 300/500 V PVC Building & Damp-Location Fixed – Conductor resistance & current-carrying capacity (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nym-j-nym-o-pvc-building-installation-sheathed-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0250-204. Values for your order are confirmed in the quotation.
Cross-section | Max. DC R₂₀ Ω/km | Current in air A (30 °C) ≈ | Voltage drop mV/A·m
1.5 mm² (AWG 16) | 13.3 | 18 | 29
2.5 mm² (AWG 14) | 7.98 | 26 | 17.5
4.0 mm² (AWG 12) | 4.95 | 34 | 10.9
6.0 mm² (AWG 10) | 3.3 | 44 | 7.3
10 mm² (AWG 8) | 1.91 | 61 | 4.2
16 mm² (AWG 6) | 1.21 | 82 | 2.7
25 mm² (AWG 4) | 0.78 | 108 | 1.7
35 mm² (AWG 2) | 0.554 | 135 | 1.2
Current ratings are for 3 loaded conductors at 30 °C ambient in free air/tray per IEC 60364-5-52 / NEC.

## Technical data
NYM-J / NYM-O 300/500 V PVC Building & Damp-Location Fixed – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nym-j-nym-o-pvc-building-installation-sheathed-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0250-204. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (Per DIN VDE 0250-204)
Key data | Operating temp. | −40…+70 °C (Continuous thermal rating)
Key data | Min. bend radius | 4 × OD (Installed / fixed routing)
Key data | Conductor | copper conductor (High-conductivity copper conductor)
Key data | Outer layer | PVC outer sheath (Extruded PVC outer sheath protective)
Key data | Standard | DIN VDE 0250-204 (DIN VDE 0250-204)
Electrical | Rated voltage / duty | 300/500 V (DIN VDE 0250-204)
Electrical | Conductor construction | Stranded copper conductor — High-conductivity copper conductor per DIN VDE 0250-204
Electrical | Primary insulation / dielectric | PVC core insulation — Extruded PVC dielectric (individual core / group layer)
Thermal | Continuous operating temperature | −40…+70 °C per DIN VDE 0250-204
Thermal | Short-circuit / peak thermal limit | +160 °C to +250 °C (5 s adiabatic limit depending on dielectric class)
Thermal | Minimum installation temperature | −5 °C (thermoplastic) / −25 °C (cross-linked or elastomer) / −40 °C (metallic)
Mechanical | Outer protection / covering | PVC outer sheath — Extruded PVC outer sheath protective layer (continuous layer)
Mechanical | Minimum bending radius | 4 × OD (installed / static routing)
Mechanical | Layer count & geometry | 4 concentric/structural layers verified by cross-section inspection
Resistance | Environmental & chemical durability | Engineered for industrial service in accordance with DIN VDE 0250-204
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing product standard | DIN VDE 0250-204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | NYM-J
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 7614.10

## Construction
NYM-J / NYM-O 300/500 V PVC Building & Damp-Location Fixed – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nym-j-nym-o-pvc-building-installation-sheathed-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0250-204. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded copper conductor | High-conductivity copper conductor per DIN VDE 0250-204 | DIN VDE 0250-204
2 | PVC core insulation | Extruded PVC dielectric (individual core / group layer) | DIN VDE 0250-204
3 | Filling compound | Extruded Filling compound protective layer (continuous layer) | DIN VDE 0250-204
4 | PVC outer sheath | Extruded PVC outer sheath protective layer (continuous layer) | DIN VDE 0250-204
| NYM-J — Standard Execution | Built to DIN VDE 0250-204 with stranded copper conductor and pvc outer sheath
| NYM-J — Custom Cross-Sections | Full range of metric mm² and AWG/kcmil conductor sizes per DIN VDE 0250-204
| NYM-J — Export Drum Supply | Supplied with EN 10204 3.1 routine dielectric & conductor resistance test certificate

## Quality and supply
NYM-J / NYM-O 300/500 V PVC Building & Damp-Location Fixed – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nym-j-nym-o-pvc-building-installation-sheathed-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0250-204. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (DIN VDE 0250-204) — DC resistance at 20 °C and geometry within DIN VDE 0250-204 class limits | Every manufactured drum / spool
Routine test | Routine dielectric / spark / structural integrity test (DIN VDE 0250-204) — Zero breakdown or structural defect over full production length | Every manufactured drum / spool
Type test | Thermal aging, mechanical & material qualification (DIN VDE 0250-204) — Full compliance with DIN VDE 0250-204 across −40…+70 °C | Type qualification & periodic sample audit
Standard / approval | DIN VDE 0250-204 Compliant
Standard / approval | EN 10204 3.1 Routine Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NYM-J <size> DIN VDE 0250-204 300/500 V CE
Supply | Delivery form: Non-returnable fumigated wooden drums or precision DIN spools
Supply | Standard lengths: 500 m · 1000 m · 2000 m drums (custom cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP