## Request a quote
Request a quotation for OGc
Specify voltage class (0.6/1 kV, 1.8/3 kV, or 3.6/6 kV), core count (1× or 3+1), conductor size (16–185 mm²), and outdoor ambient temperature range.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ogc-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OGc Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ogc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Voltage & Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| OGc 1.8/3 kV 3×16+1×10 | 1.8/3 kV 3×16+1×10 | 16 | 29.2 | 557 | 1340 | 175 | 0.6/1 kV & 1.8/3 kV OGc heavy open-cast & quarry feeders
| OGc 1.8/3 kV 3×25+1×16 | 1.8/3 kV 3×25+1×16 | 25 | 33.5 | 874 | 1840 | 201 | 0.6/1 kV & 1.8/3 kV OGc heavy open-cast & quarry feeders
| OGc 1.8/3 kV 3×35+1×16 | 1.8/3 kV 3×35+1×16 | 35 | 36.8 | 1162 | 2290 | 221 | 0.6/1 kV & 1.8/3 kV OGc heavy open-cast & quarry feeders
| OGc 1.8/3 kV 3×50+1×25 | 1.8/3 kV 3×50+1×25 | 50 | 41.6 | 1680 | 3080 | 250 | 0.6/1 kV & 1.8/3 kV OGc heavy open-cast & quarry feeders
| OGc 1.8/3 kV 3×70+1×35 | 1.8/3 kV 3×70+1×35 | 70 | 46.8 | 2352 | 4020 | 281 | 0.6/1 kV & 1.8/3 kV OGc heavy open-cast & quarry feeders
| OGc 1.8/3 kV 3×95+1×50 | 1.8/3 kV 3×95+1×50 | 95 | 52.4 | 3216 | 5190 | 314 | 0.6/1 kV & 1.8/3 kV OGc heavy open-cast & quarry feeders
| OGc 3.6/6 kV 1×50 | 3.6/6 kV 1×50 | 50 | 21.5 | 480 | 820 | 129 | 3.6/6 kV OGc medium-voltage open-cast excavator feeders
| OGc 3.6/6 kV 1×95 | 3.6/6 kV 1×95 | 95 | 26.2 | 912 | 1390 | 157 | 3.6/6 kV OGc medium-voltage open-cast excavator feeders
| OGc 3.6/6 kV 1×150 | 3.6/6 kV 1×150 | 150 | 30.8 | 1440 | 2040 | 185 | 3.6/6 kV OGc medium-voltage open-cast excavator feeders
| OGc 3.6/6 kV 3×25+1×16 | 3.6/6 kV 3×25+1×16 | 25 | 38.4 | 874 | 2210 | 230 | 3.6/6 kV OGc medium-voltage open-cast excavator feeders
| OGc 3.6/6 kV 3×50+1×25 | 3.6/6 kV 3×50+1×25 | 50 | 46.2 | 1680 | 3510 | 277 | 3.6/6 kV OGc medium-voltage open-cast excavator feeders
| OGc 3.6/6 kV 3×95+1×50 | 3.6/6 kV 3×95+1×50 | 95 | 57 | 3216 | 5740 | 342 | 3.6/6 kV OGc medium-voltage open-cast excavator feeders
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90105 / PN-89/E-90143.

## Electrical & ampacity data
OGc Cable – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ogc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
1.8/3 kV 3×16+1×10 | 1.21 | 93 | 79 | 101 | 6500
1.8/3 kV 3×25+1×16 | 0.78 | 123 | 105 | 114 | 6500
1.8/3 kV 3×35+1×16 | 0.554 | 152 | 129 | 129 | 6500
1.8/3 kV 3×50+1×25 | 0.386 | 189 | 161 | 150 | 6500
1.8/3 kV 3×70+1×35 | 0.272 | 233 | 198 | 180 | 6500
1.8/3 kV 3×95+1×50 | 0.206 | 282 | 240 | 216 | 6500
3.6/6 kV 1×50 | 0.386 | 189 | 161 | 150 | 11000
3.6/6 kV 1×95 | 0.206 | 282 | 240 | 216 | 11000
3.6/6 kV 1×150 | 0.129 | 374 | 318 | 268 | 11000
3.6/6 kV 3×25+1×16 | 0.78 | 123 | 105 | 114 | 11000
3.6/6 kV 3×50+1×25 | 0.386 | 189 | 161 | 150 | 11000
3.6/6 kV 3×95+1×50 | 0.206 | 282 | 240 | 216 | 11000
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
OGc Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ogc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 & 3.6/6 kV (Also available in 0.6/1 kV heavy grade)
Key data | Conductor max. | +90 °C (Heat-resistant 'c' EPR · +250 °C SC)
Key data | Ambient (outdoor) | -40 to +60 °C (Cold-climate open-pit quarry duty)
Key data | Min. bend R | 6 × D / 10 × D (Fixed routing / mobile trailing)
Key data | Core layout | 1, 3 or 4 cores (16 mm² to 185 mm² power feeders)
Key data | Weathering | UV & ozone proof (Open-pit year-round outdoor exposure)
Electrical | Rated voltage U0/U | 0.6/1 kV, 1.8/3 kV, or 3.6/6 kV
Electrical | Maximum system voltage Um | 1.2 kV, 3.6 kV, or 7.2 kV
Electrical | Routine AC test voltage | 3.0 kV / 6.5 kV / 11.0 kV rms
Electrical | Specific insulation resistance | ≥ 500 MΩ·km at +20 °C
Electrical | Nominal frequency | 50 / 60 Hz
Electrical | Conductor stranding class | IEC 60228 Class 5
Thermal | Max. conductor operating temp. | +90 °C continuous ('c' EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Outdoor mobile ambient range | -40 °C to +60 °C
Thermal | Fixed ambient range | -50 °C to +60 °C
Thermal | Min. laying temperature | -25 °C
Thermal | Emergency overload temp. | +105 °C
Mechanical | Min. bend radius (fixed) | 6 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 10 × overall diameter (D)
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Bench dragging abrasion | Heavy-wall elastomer outer jacket
Mechanical | Cold-impact resilience | No cracking down to -40 °C
Mechanical | Tear strength | ≥ 15 N/mm
Resistance | UV & sunlight resistance | Carbon-stabilised black elastomer
Resistance | Ozone resistance | Ozone-inert EPR insulation & sheath
Resistance | Oil & diesel resistance | EN 60811-404 resistant
Resistance | Flame retardance | IEC 60332-1-2 self-extinguishing
Resistance | Water & mud exposure | Suitable for flooded quarry benches
Resistance | Halogen status | Chloroprene elastomer
Standards | Primary product standard | PN-G-90105 / PN-89/E-90143
Standards | Conductor standard | IEC 60228 Class 5
Standards | Flame test standard | PN-EN 60332-1-2
Standards | Open-cast mining rules | Polish surface mining equipment code
Standards | Environmental compliance | CE & RoHS compliant
Standards | Quality certification | EN 10204 3.1 mill certificate
Identification | Core identification | HD 308 colours or numbered cores
Identification | Protective earth core | Green/yellow
Identification | Outer sheath colour | Black
Identification | Sheath marking | TEBAOFLEX OGc [U0/U] [n×mm²] CE
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
OGc Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ogc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / PN-89/E-90143. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Class 5 fine-stranded plain or tinned annealed copper wire | IEC 60228 Class 5
2 | +90 °C EPR dielectric ('c') | Ozone- and heat-resistant cross-linked ethylene-propylene rubber compound | PN-G-90105
3 | Elastomeric inner filler & bedding | Extruded rubber inner covering providing circular cross-section and impact cushioning | PN-89/E-90143
4 | Heavy-duty open-cast outer rubber | Abrasion-, oil-, UV-, and cold-resistant polychloroprene/chlorosulphonated elastomer | PN-G-90105
| OGc 1.8/3 kV (3+1 cores) | Four-core (3 phase + reduced PE) trailing feeder for open-pit quarry machinery and belt conveyor stations.
| OGc 3.6/6 kV (1× or 3×) | Single-core and three-core medium-voltage flexible rubber cables for mobile substation jumpers and excavators.

## Quality and supply
OGc Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ogc-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage withstand test — 6.5 kV rms (1.8/3 kV) or 11.0 kV rms (3.6/6 kV) for 5 minutes | Every drum
Routine test | Conductor DC resistance — Complies with IEC 60228 Class 5 at 20 °C | Every drum
Sample test | Cold-bend & cold-impact test at -40 °C — No sheath or insulation cracking under sub-zero flexing | Per batch
Type test | Ozone, UV & oil resistance test — Passes EN 60811-403 ozone test and EN 60811-404 oil immersion | Type approval
Standard / approval | PN-G-90105 / PN-89/E-90143
Standard / approval | IEC 60332-1-2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX OGc [U0/U] [n×mm²] PN-G-90105 CE
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP