## Request a quote
Request a quotation for OPPC
Application engineer · optical & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/optical-phase-conductor-oppc-overhead-power-transmission-composite-fibre-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OPPC Optical Phase Conductor (OPPC) Overhead Power Transmission – Dimensions, ampacity & RTS (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/optical-phase-conductor-oppc-overhead-power-transmission-composite-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-4-20 / IEEE 1138 / IEC 61089. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Matched ACSR & fibres | Outer Ø mm | Weight ≈ kg/km | RTS kN | DC R @ 20 °C Ω/km | Ampacity A | Series
| OPPC-24B1-70/10 | ACSR 70/10 · 24F G.652.D | 11.4 | 275 | 26 | 0.41 | 245 | 10–66 kV Medium-Voltage OPPC (70–150 mm²)
| OPPC-24B1-120/20 | ACSR 120/20 · 24F G.652.D | 15.2 | 495 | 46 | 0.238 | 365 | 10–66 kV Medium-Voltage OPPC (70–150 mm²)
| OPPC-48B1-150/25 | ACSR 150/25 · 48F G.652.D | 17.1 | 610 | 56 | 0.192 | 425 | 10–66 kV Medium-Voltage OPPC (70–150 mm²)
| OPPC-48B1-185/30 | ACSR 185/30 · 48F G.652.D | 19 | 745 | 68 | 0.154 | 495 | 66–220 kV High-Voltage OPPC (185–400 mm²)
| OPPC-48B1-240/40 | ACSR 240/40 · 48F G.652.D | 21.6 | 965 | 86 | 0.119 | 590 | 66–220 kV High-Voltage OPPC (185–400 mm²)
| OPPC-96B1-400/50 | ACSR 400/50 · 96F G.652.D | 27.6 | 1510 | 132 | 0.072 | 840 | 66–220 kV High-Voltage OPPC (185–400 mm²)
Continuous ampacity calculated at +80 °C conductor, +35 °C ambient, 0.6 m/s wind and 1000 W/m² solar radiation per IEC 61597.

## Technical data
OPPC Optical Phase Conductor (OPPC) Overhead Power Transmission – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/optical-phase-conductor-oppc-overhead-power-transmission-composite-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-4-20 / IEEE 1138 / IEC 61089. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Fibre count | 12 to 96 fibres (G.652.D / G.655 in 316L FIMT)
Key data | Cross-section | 70 to 400 mm² (ACSR / AAAC phase-matched)
Key data | Continuous amp. | 245 to 840 A (Continuous phase current)
Key data | Breaking load | 42 to 138 kN (Rated Tensile Strength (RTS))
Key data | Operating temp. | -40 to +90 °C (+200 °C short-circuit peak)
Key data | Fibre loss | ≤ 0.35 / 0.21 (dB/km @ 1310 / 1550 nm)
Electrical | Continuous current (ampacity) | 245 A (OPPC-70) to 840 A (OPPC-400) per IEC 61597
Electrical | DC resistance @ 20 °C | 0.072 to 0.410 Ω/km
Electrical | Short-circuit capacity (I²t) | 25 to 260 kA²·s (0.5 s to +200 °C)
Thermal | Continuous operating temp. | -40 °C to +90 °C (continuous phase current)
Thermal | Short-circuit peak temp. | Up to +200 °C (0.5 s fault duration)
Thermal | Linear expansion coeff. | 17.8 to 19.6 × 10⁻⁶ /K (ACSR-matched)
Mechanical | Rated Tensile Strength (RTS) | 42 kN to 138 kN
Mechanical | Modulus of elasticity | 68 to 88 GPa (matched to companion phases)
Mechanical | Crush resistance | ≥ 10,000 N / 100 mm
Mechanical | Min. bend radius | 20 × OD (static) · 30 × OD (stringing sheave)
Optical | Fibre specification | ITU-T G.652.D / G.655 (high-temp +125 °C coating opt)
Optical | Attenuation @ 1310 / 1550 nm | ≤ 0.35 dB/km / ≤ 0.21 dB/km
Optical | Excess fibre length (EFL) | 0.25 % to 0.40 % inside 316L FIMT
Resistance | Hermeticity & moisture | 100 % eddy-current tested 316L welded FIMT
Resistance | Aeolian vibration | 10⁸ cycles at 20 % RTS without wire or fibre break
Resistance | HV isolation at joints | Porcelain/silicone composite HV optical insulator boxes
Standards | OPPC standard | IEC 60794-4-20 Aerial Optical Phase Conductors
Standards | Conductor standard | IEC 61089 · IEC 61232 (ACS) · IEC 60889
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Outer appearance | Bare stranded aluminum phase conductor
Identification | Fibre colour code | TIA-598-D 12-colour + ring-coded bundles
Identification | Customs tariff (HS) | 8544.7000

## Construction
OPPC Optical Phase Conductor (OPPC) Overhead Power Transmission – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/optical-phase-conductor-oppc-overhead-power-transmission-composite-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-4-20 / IEEE 1138 / IEC 61089. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Single-mode optical fibres + high-temp gel | 12 to 96 ITU-T G.652.D / G.655 single-mode fibres (+ optional OM3/SM sensing fibres) in +200 °C silicone-free thixotropic compound | ≤ 0.35 dB/km @ 1310 nm · ≤ 0.21 dB/km @ 1550 nm
2 | Laser-welded 316L stainless-steel FIMT | Hermetically welded AISI 304L/316L stainless-steel tube (central or inner-layer stranded) with 0.25–0.40 % EFL
3 | Inner Aluminum-Clad Steel (ACS) strength core | Concentric-lay Aluminum-Clad Steel (20SA–40SA per IEC 61232) or galvanized steel core wires
4 | Outer EC Aluminum / AAAC phase conductor wires | 1 to 3 layers of hard-drawn 1350-H19 Aluminum (IEC 60889) or 6201-T81 Aluminum Alloy (IEC 60104) wires
| OPPC-70 to OPPC-150 (10–66 kV) | Matched to LGJ-70/10, 95/15, 120/20 & 150/25 ACSR phase conductors with 24–48 fibres
| OPPC-185 to OPPC-400 (66–220 kV) | Matched to Drake / Lynx / Zebra ACSR phase conductors with 48–96 fibres and HV insulator splice boxes

## Quality and supply
OPPC Optical Phase Conductor (OPPC) Overhead Power Transmission – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/optical-phase-conductor-oppc-overhead-power-transmission-composite-fibre-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60794-4-20 / IEEE 1138 / IEC 61089. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % eddy-current FIMT weld, DC resistance & OTDR test — Zero tube pinholes, DC R within IEC 61089, α ≤ 0.35 / 0.21 dB/km | Every manufactured drum length
Type test | Continuous +90 °C thermal aging & +200 °C short-circuit test — Δα ≤ 0.05 dB/km after thermal cycling and rated I²t fault pulse | Type qualification
Type test | Stress-strain, creep & aeolian vibration fatigue — 10⁸ vibration cycles and tensile loading to RTS per IEC 60794-4-20 | Type qualification
Standard / approval | IEC 60794-4-20 OPPC Standard
Standard / approval | IEC 61089 & IEEE 1138
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Stamped drum tag: TEBAOFLEX OPPC-<COUNT>B1-<AREA> IEC 60794-4-20
Supply | Delivery form: Fumigated export wooden or steel drums
Supply | Standard drum lengths: 1000 m · 2000 m · 4000 m (or custom cut lengths)
Supply | MOQ: 500 m (standard) · 1000 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP