## Request a quote
Request a quotation for OnG1
Specify core count (7 to 37 cores), conductor cross-section (1.5, 2.5, or 4 mm²), required drum length, and whether underground WUG documentation is needed.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ong1-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OnG1 Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90103 / ZN-TF-202. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| OnG1 7×1.5 | 7×1.5 | 1.5 | 16.5 | 101 | 390 | 99 | Standard OnG1 configurations
| OnG1 10×1.5 | 10×1.5 | 1.5 | 19.8 | 144 | 540 | 119 | Standard OnG1 configurations
| OnG1 12×1.5 | 12×1.5 | 1.5 | 20.6 | 173 | 605 | 124 | Standard OnG1 configurations
| OnG1 14×1.5 | 14×1.5 | 1.5 | 21.8 | 202 | 680 | 131 | Standard OnG1 configurations
| OnG1 19×1.5 | 19×1.5 | 1.5 | 24.5 | 274 | 870 | 147 | Standard OnG1 configurations
| OnG1 24×1.5 | 24×1.5 | 1.5 | 28.2 | 346 | 1120 | 169 | Standard OnG1 configurations
| OnG1 30×1.5 | 30×1.5 | 1.5 | 30.5 | 432 | 1360 | 183 | Standard OnG1 configurations
| OnG1 37×1.5 | 37×1.5 | 1.5 | 33 | 533 | 1620 | 198 | Standard OnG1 configurations
| OnG1 7×2.5 | 7×2.5 | 2.5 | 18.4 | 168 | 505 | 110 | Standard OnG1 configurations
| OnG1 12×2.5 | 12×2.5 | 2.5 | 23.2 | 288 | 810 | 139 | Standard OnG1 configurations
| OnG1 19×2.5 | 19×2.5 | 2.5 | 27.6 | 456 | 1190 | 166 | Standard OnG1 configurations
| OnG1 24×2.5 | 24×2.5 | 2.5 | 31.8 | 576 | 1530 | 191 | Standard OnG1 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90103 / ZN-TF-202.

## Electrical & ampacity data
OnG1 Cable – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90103 / ZN-TF-202. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
7×1.5 | 13.3 | 19 | 16 | 80 | 3000
10×1.5 | 13.3 | 19 | 16 | 80 | 3000
12×1.5 | 13.3 | 19 | 16 | 80 | 3000
14×1.5 | 13.3 | 19 | 16 | 80 | 3000
19×1.5 | 13.3 | 19 | 16 | 80 | 3000
24×1.5 | 13.3 | 19 | 16 | 80 | 3000
30×1.5 | 13.3 | 19 | 16 | 80 | 3000
37×1.5 | 13.3 | 19 | 16 | 80 | 3000
7×2.5 | 7.98 | 26 | 22 | 82 | 3000
12×2.5 | 7.98 | 26 | 22 | 82 | 3000
19×2.5 | 7.98 | 26 | 22 | 82 | 3000
24×2.5 | 7.98 | 26 | 22 | 82 | 3000
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
OnG1 Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90103 / ZN-TF-202. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (U0/U AC · Um 1.2 kV)
Key data | Conductor max. | +70 °C (Continuous · +200 °C short-circuit)
Key data | Ambient (flex) | -25 to +60 °C (Mobile underground & surface duty)
Key data | Min. bend R | 6 × D / 10 × D (Fixed installation / mobile flexing)
Key data | Core count | 7 to 37 cores (1.5 mm² to 4 mm² control cores)
Key data | Flame test | IEC 60332-1-2 (PN-G-90100 mine flame-retardant PCP)
Electrical | Rated voltage U0/U | 0.6/1 kV AC
Electrical | Maximum system voltage Um | 1.2 kV AC (1.5 kV DC)
Electrical | Routine AC test voltage | 3.0 kV rms / 5 min
Electrical | Specific volume resistivity | ≥ 10¹² Ω·cm at +20 °C
Electrical | Nominal frequency | 50 / 60 Hz & DC control
Electrical | Conductor resistance class | IEC 60228 Class 5
Thermal | Max. conductor operating temp. | +70 °C continuous
Thermal | Max. short-circuit temperature | +200 °C (max. 5 s)
Thermal | Mobile ambient range | -25 °C to +60 °C
Thermal | Fixed ambient range | -40 °C to +60 °C
Thermal | Min. installation temperature | -15 °C
Thermal | Thermal overload margin | +85 °C emergency rating
Mechanical | Min. bend radius (fixed) | 6 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 10 × overall diameter (D)
Mechanical | Max. tensile pull on copper | 15 N/mm² total conductor area
Mechanical | Impact & crush resistance | Heavy underground gallery duty
Mechanical | Abrasion resistance | High-tear PCP outer compound
Mechanical | Torsional stress rating | Not intended for free torsion
Resistance | Flame retardance | IEC 60332-1-2 / PN-G-90100
Resistance | Mineral oil resistance | EN 60811-404 oil-resistant PCP
Resistance | Mine water & humidity | Resistant to acidic/alkaline mine water
Resistance | Ozone & weathering | Ozone-resistant EPR & PCP compounds
Resistance | Chemical & grease exposure | Resistant to hydraulic emulsions
Resistance | Halogen content | Polychloroprene (contains halogens)
Standards | Primary product standard | PN-G-90103 / ZN-TF-202
Standards | General mining series norm | PN-G-90100
Standards | Conductor stranding norm | IEC 60228 / PN-EN 60228 Class 5
Standards | Flame propagation test | PN-EN 60332-1-2
Standards | Mine authority compliance | WUG Poland underground mining rules
Standards | Quality assurance | ISO 9001 & EN 10204 3.1
Identification | Core identification | White numbers on black cores + G/Y
Identification | Protective earth core | Green/yellow in outer layer
Identification | Outer sheath colour | Black (optional yellow mining stripe)
Identification | Sheath marking method | Embossed or ink-printed metre legend
Identification | Voltage stamp | 0.6/1 kV PN-G-90103
Identification | Traceability code | Batch number & production year

## Construction
OnG1 Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90103 / ZN-TF-202. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Plain or tinned annealed copper wire, Class 5 fine-stranded | IEC 60228 Class 5
2 | EPR core insulation | Cross-linked ethylene-propylene elastomer (EPR) compound | PN-G-90103
3 | Concentric multi-core lay-up | Numbered black cores plus green/yellow earth core laid in concentric layers with rubber | PN-G-90103
4 | Separating binding tape | Non-hygroscopic synthetic textile wrapping tape over laid-up assembly
5 | Outer protective sheath | Heavy-duty flame-retardant, oil-resistant polychloroprene (PCP / CR) mining compound | PN-G-90100 / PN-G-90103
| OnG1 7–14 cores | Compact multi-core control configurations (1.5–4 mm²) for conveyor interlocks and local control stations.
| OnG1 19–37 cores | High-density multi-core signalling and telemetry cables (1.5–2.5 mm²) for mining switchgear panels.

## Quality and supply
OnG1 Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90103 / ZN-TF-202. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage withstand test — 3.0 kV rms for 5 minutes without breakdown | Every manufactured drum
Routine test | Conductor DC resistance — Complies with IEC 60228 Class 5 maximum at 20 °C | 100 % of cores
Sample test | Insulation & sheath mechanical properties — Tensile strength and elongation before/after ageing per PN-G-90100 | Per production batch
Type test | Vertical flame propagation & oil immersion — Passes IEC 60332-1-2 flame test and EN 60811-404 oil immersion | Type qualification
Standard / approval | PN-G-90103 / PN-G-90100
Standard / approval | IEC 60332-1-2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX OnG1 0.6/1 kV [n×mm²] PN-G-90103
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP