## Request a quote
Request a quotation for OnG
Application engineer · Polish PN & VDE mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ong-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OnG Cable – Dimensions & weights (24)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-91/E-90103 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| OnG 1×25 (0.6/1 kV) | 1×25 | 4 | 11.6 | 12.6 | 240 | 335 | 50 | OnG Single-Core 0.6/1 kV Mining & Industrial Power Leads (25–240 mm²)
| OnG 1×50 (0.6/1 kV) | 1×50 | 1 | 14.9 | 16.2 | 480 | 610 | 65 | OnG Single-Core 0.6/1 kV Mining & Industrial Power Leads (25–240 mm²)
| OnG 1×95 (0.6/1 kV) | 1×95 | 3/0 | 19.3 | 21 | 912 | 1110 | 84 | OnG Single-Core 0.6/1 kV Mining & Industrial Power Leads (25–240 mm²)
| OnG 1×150 (0.6/1 kV) | 1×150 | 300 kcmil | 23.6 | 25.6 | 1440 | 1710 | 102 | OnG Single-Core 0.6/1 kV Mining & Industrial Power Leads (25–240 mm²)
| OnG 1×240 (0.6/1 kV) | 1×240 | 500 kcmil | 29 | 31.5 | 2304 | 2660 | 126 | OnG Single-Core 0.6/1 kV Mining & Industrial Power Leads (25–240 mm²)
| OnG 3×1.5 | 3G1.5 | 16 | 9.8 | 10.6 | 43 | 155 | 42 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×1.5 | 4G1.5 | 16 | 10.7 | 11.6 | 58 | 190 | 46 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 5×1.5 | 5G1.5 | 16 | 11.8 | 12.8 | 72 | 235 | 51 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 3×2.5 | 3G2.5 | 14 | 11.2 | 12.2 | 72 | 220 | 49 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×2.5 | 4G2.5 | 14 | 12.3 | 13.4 | 96 | 270 | 54 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 5×2.5 | 5G2.5 | 14 | 13.6 | 14.8 | 120 | 330 | 59 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×4 | 4G4 | 12 | 14.4 | 15.6 | 154 | 390 | 62 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×6 | 4G6 | 10 | 16.1 | 17.5 | 230 | 520 | 70 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×10 | 4G10 | 8 | 20.1 | 21.8 | 384 | 860 | 87 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×16 | 4G16 | 6 | 23.2 | 25.2 | 614 | 1210 | 101 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×25 | 4G25 | 4 | 27.8 | 30.2 | 960 | 1780 | 121 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×35 | 4G35 | 2 | 31.3 | 34 | 1344 | 2350 | 136 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×50 | 4G50 | 1 | 36.3 | 39.5 | 1920 | 3220 | 158 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×70 | 4G70 | 2/0 | 41 | 44.6 | 2688 | 4310 | 178 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 4×95 | 4G95 | 3/0 | 46.2 | 50.2 | 3648 | 5650 | 201 | OnG Multicore Power Cables (3G1.5–4G95)
| OnG 7×1.5 | 7G1.5 | 16 | 14 | 15.2 | 101 | 330 | 61 | OnG Multicore Mining Control & Signalling Cables (7G1.5–12G2.5)
| OnG 12×1.5 | 12G1.5 | 16 | 17.8 | 19.4 | 173 | 520 | 78 | OnG Multicore Mining Control & Signalling Cables (7G1.5–12G2.5)
| OnG 7×2.5 | 7G2.5 | 14 | 16.4 | 17.8 | 168 | 470 | 71 | OnG Multicore Mining Control & Signalling Cables (7G1.5–12G2.5)
| OnG 12×2.5 | 12G2.5 | 14 | 20.8 | 22.6 | 288 | 760 | 90 | OnG Multicore Mining Control & Signalling Cables (7G1.5–12G2.5)
Dimensions and weights are typical values per PN-91/E-90103 / PN-89/E-90143. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
OnG Cable – Electrical & current ratings (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-91/E-90103 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
4 | 12 | 4.95 | 41 | 34
6 | 10 | 3.3 | 53 | 44
10 | 8 | 1.91 | 74 | 61
16 | 6 | 1.21 | 99 | 82
25 | 4 | 0.78 | 131 | 108
35 | 2 | 0.554 | 162 | 135
50 | 1 | 0.386 | 202 | 168
70 | 2/0 | 0.272 | 250 | 207
95 | 3/0 | 0.206 | 301 | 250
150 | 300 kcmil | 0.129 | 404 | 335
240 | 500 kcmil | 0.08 | 540 | 453
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
OnG Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-91/E-90103 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Also 450/750 V · 2.5/3.0 kV test)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −25…+70 °C (Flexing (−40…+70 °C fixed))
Key data | Bending radius | 4–6 × OD (4 × OD fixed · 6 × OD flexing)
Key data | Compounds | GIE1 / ON-3 (EPR core · flame/oil PCP sheath)
Key data | Size range | 1.5–240 mm² (1 to 19 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 450/750 V or 0.6/1 kV (600/1000 V AC)
Electrical | AC test voltage | 2500 V AC (450/750 V) · 3000 V AC (0.6/1 kV), 50 Hz
Electrical | Conductor stranding | PN-EN 60228 / IEC 60228 Class 5 flexible copper
Electrical | Insulation resistance | ≥ 20 MΩ·km at +20 °C
Electrical | Current rating basis | 90 °C EPR thermoset conductor rating
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −25 °C to +70 °C
Thermal | Temperature, fixed | −40 °C to +70 °C
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, moving | 6 × overall diameter
Mechanical | Max. tensile load | 15 N/mm² of total copper cross-section
Mechanical | Mechanical impact class | Heavy mining & industrial trailing duty ('Oponowy Górniczy')
Resistance | Flame retardance ('n') | PN-EN 60332-1-2 / IEC 60332-1-2 self-extinguishing mining sheath
Resistance | Oil & grease resistance ('n') | PN-EN 60811-404 mineral oil, diesel & hydraulic emulsion resistant
Resistance | Mine water & humidity | Resistant to underground dampness, mud and coal dust
Resistance | Weather & ozone | Ozone-resistant GIE1 EPR and ON-3 polychloroprene sheath
Standards | Construction standards | PN-91/E-90103 & PN-89/E-90143
Standards | European equivalent | Comparable to DIN VDE 0250-812 NSSHÖU / EN 50525-2-21 H07RN-F
Standards | Conductor standard | PN-EN 60228 / IEC 60228 Class 5
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black (or yellow/orange for mining visibility)
Identification | Core identification | Up to 5 cores: HD 308 S2 colour code · ≥ 6 cores: numbered + GN/YE
Identification | Sheath marking | TEBAOFLEX OnG [Size] 450/750V or 0.6/1kV PN-91/E-90103 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
OnG Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-91/E-90103 / PN-89/E-90143. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded annealed bare or tinned copper wire (PN-EN 60228 / IEC 60228 Class 5) | PN-EN 60228 Class 5
2 | Separator foil | Polyester or non-woven tape over the conductor preventing elastomer adhesion | PN-91/E-90103
3 | EPR core insulation (GIE1) | Cross-linked ethylene-propylene rubber compound Type GIE1 / EI4-EI7 (+90 °C rated) | PN-91/E-90103
4 | Inner elastomeric filling | Extruded rubber filler or inner sheath on heavy multicore sizes for impact resistance | PN-91/E-90103
5 | Mining PCP outer sheath (ON-3) | Cross-linked polychloroprene (neoprene) compound Type ON-3 / EM2, flame-retardant and oil-resistant | PN-91/E-90103 · IEC 60332-1-2 · EN 60811-404
| OnG 450/750 V (2×1.5 to 5×16 & 7–19C) | Light-to-medium mining and auxiliary control cables to PN-91/E-90103
| OnG 0.6/1 kV (1×10–1×240 & 3×1.5–5×95) | Heavy-duty 0.6/1 kV mining power and trailing cables to PN-89/E-90143 / WT-TFK

## Quality and supply
OnG Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ong-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-91/E-90103 / PN-89/E-90143. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 3.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — PN-91/E-90103 / PN-89/E-90143 | Type approval
Standard / approval | PN-91/E-90103 / PN-89/E-90143
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX OnG [Size] 0.6/1 kV PN-91/E-90103 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request