## Request a quote
Request a quotation for OnGcekgż-G
Specify voltage rating (3.6/6 kV or 6/10 kV), phase cross-section (16–120 mm²), pilot core arrangement, and outer sheath colour (red or black).
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ongcekgz-g-screened-mv-mining-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OnGcekgż-G Screened MV Mining Rubber Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekgz-g-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-210. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Voltage & Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| OnGcekgż-G 3.6/6 kV 3×16+1×16+1×6 | 3.6/6 kV 3×16+1×16+1×6 | 16 | 39.5 | 672 | 2120 | 237 | 3.6/6 kV (Um 7.2 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 3.6/6 kV 3×25+1×16+1×6 | 3.6/6 kV 3×25+1×16+1×6 | 25 | 43.2 | 931 | 2590 | 259 | 3.6/6 kV (Um 7.2 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 3.6/6 kV 3×35+1×16+1×6 | 3.6/6 kV 3×35+1×16+1×6 | 35 | 46 | 1219 | 3040 | 276 | 3.6/6 kV (Um 7.2 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 3.6/6 kV 3×50+1×25+1×6 | 3.6/6 kV 3×50+1×25+1×6 | 50 | 50.8 | 1738 | 3840 | 305 | 3.6/6 kV (Um 7.2 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 3.6/6 kV 3×70+1×35+1×6 | 3.6/6 kV 3×70+1×35+1×6 | 70 | 55.6 | 2410 | 4790 | 334 | 3.6/6 kV (Um 7.2 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 3.6/6 kV 3×95+1×50+1×6 | 3.6/6 kV 3×95+1×50+1×6 | 95 | 61.2 | 3274 | 6010 | 367 | 3.6/6 kV (Um 7.2 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 6/10 kV 3×25+1×16+1×6 | 6/10 kV 3×25+1×16+1×6 | 25 | 47.5 | 931 | 2980 | 285 | 6/10 kV (Um 12 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 6/10 kV 3×35+1×16+1×6 | 6/10 kV 3×35+1×16+1×6 | 35 | 50.4 | 1219 | 3460 | 302 | 6/10 kV (Um 12 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 6/10 kV 3×50+1×25+1×6 | 6/10 kV 3×50+1×25+1×6 | 50 | 55.2 | 1738 | 4310 | 331 | 6/10 kV (Um 12 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 6/10 kV 3×70+1×35+1×6 | 6/10 kV 3×70+1×35+1×6 | 70 | 60 | 2410 | 5320 | 360 | 6/10 kV (Um 12 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 6/10 kV 3×95+1×50+1×6 | 6/10 kV 3×95+1×50+1×6 | 95 | 65.8 | 3274 | 6620 | 395 | 6/10 kV (Um 12 kV) OnGcekgż-G medium-voltage mining
| OnGcekgż-G 6/10 kV 3×120+1×50+1×6 | 6/10 kV 3×120+1×50+1×6 | 120 | 70.2 | 3994 | 7740 | 421 | 6/10 kV (Um 12 kV) OnGcekgż-G medium-voltage mining
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90105 / ZN-TF-210.

## Electrical & ampacity data
OnGcekgż-G Screened MV Mining Rubber Cable – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekgz-g-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-210. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
3.6/6 kV 3×16+1×16+1×6 | 1.21 | 93 | 79 | 101 | 11000
3.6/6 kV 3×25+1×16+1×6 | 0.78 | 123 | 105 | 114 | 11000
3.6/6 kV 3×35+1×16+1×6 | 0.554 | 152 | 129 | 129 | 11000
3.6/6 kV 3×50+1×25+1×6 | 0.386 | 189 | 161 | 150 | 11000
3.6/6 kV 3×70+1×35+1×6 | 0.272 | 233 | 198 | 180 | 11000
3.6/6 kV 3×95+1×50+1×6 | 0.206 | 282 | 240 | 216 | 11000
6/10 kV 3×25+1×16+1×6 | 0.78 | 123 | 105 | 114 | 17000
6/10 kV 3×35+1×16+1×6 | 0.554 | 152 | 129 | 129 | 17000
6/10 kV 3×50+1×25+1×6 | 0.386 | 189 | 161 | 150 | 17000
6/10 kV 3×70+1×35+1×6 | 0.272 | 233 | 198 | 180 | 17000
6/10 kV 3×95+1×50+1×6 | 0.206 | 282 | 240 | 216 | 17000
6/10 kV 3×120+1×50+1×6 | 0.161 | 326 | 277 | 252 | 17000
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
OnGcekgż-G Screened MV Mining Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekgz-g-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-210. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 & 6/10 kV (Medium-voltage underground mining)
Key data | Stress control | Triple 'ekg' (Inner/outer semicon + Cu/rubber screen)
Key data | Conductor max. | +90 °C (MV EPR dielectric · +250 °C SC)
Key data | Min. bend R | 6 × D / 10 × D (Fixed installation / mobile trailing)
Key data | Phase size | 16–120 mm² (Plus PE & pilot control core(s) 'ż')
Key data | AC test voltage | 11 kV / 17 kV (5 min routine dielectric test)
Electrical | Rated voltage U0/U | 3.6/6 kV or 6/10 kV AC
Electrical | Maximum system voltage Um | 7.2 kV or 12.0 kV AC
Electrical | Routine AC test voltage | 11 kV (3.6/6 kV) / 17 kV (6/10 kV)
Electrical | Partial discharge level | ≤ 20 pC at 1.5 × U0
Electrical | Pilot core rated voltage | 250 V AC
Electrical | Nominal frequency | 50 / 60 Hz
Thermal | Max. conductor operating temp. | +90 °C continuous ('c' MV EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range | -25 °C to +60 °C
Thermal | Fixed ambient range | -40 °C to +60 °C
Thermal | Min. installation temperature | -15 °C
Thermal | Emergency overload temp. | +105 °C
Mechanical | Min. bend radius (fixed) | 6 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 10 × overall diameter (D)
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Crush & impact resistance | Heavy underground '-G' PCP sheath
Mechanical | Tear resistance | ≥ 15 N/mm per PN-G-90105
Mechanical | Flexing duty | Mobile substation & face trailing
Resistance | Flame retardance | IEC 60332-1-2 / PN-G-90100 '-G'
Resistance | Mineral oil & hydraulic fluid | EN 60811-404 resistant PCP
Resistance | Ozone & corona discharge | PD-free triple-extruded MV EPR
Resistance | Mine water & humidity | Acidic/alkaline mine water resistant
Resistance | Abrasion & rockfall | Thick-wall polychloroprene jacket
Resistance | Halogen status | Polychloroprene elastomer
Standards | Primary product standard | PN-G-90105 / ZN-TF-210
Standards | Mining series base standard | PN-G-90100
Standards | Conductor standard | IEC 60228 Class 5
Standards | Flame propagation test | PN-EN 60332-1-2
Standards | Mining authority compliance | WUG Poland MV underground rules
Standards | Quality certification | EN 10204 3.1 + PD test report
Identification | Phase core identification | Numbered 1, 2, 3
Identification | Pilot core identification | Screened auxiliary control core(s)
Identification | Outer sheath colour | Red (MV warning) or black
Identification | Sheath marking | OnGcekgż-G [U0/U] [3×S+So+s] PN-G-90105
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Factory drum & HV test serial

## Construction
OnGcekgż-G Screened MV Mining Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekgz-g-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-210. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper phase conductor | Class 5 fine-stranded plain or tinned annealed copper wire | IEC 60228 Class 5
2 | Inner conductor stress-control screen | Extruded semi-conductive rubber layer smoothing conductor strand electric field | PN-G-90105
3 | Medium-voltage +90 °C EPR dielectric | Ozone- and partial-discharge-resistant cross-linked ethylene-propylene rubber | PN-G-90105
4 | Outer semi-conductive & composite | Vulcanised semi-conductive rubber layer combined with copper/elastomeric phase screening | PN-G-90105
5 | Pilot core(s) ('ż') & earth conductor | Screened pilot control core(s) and bare flexible copper protective earth conductor | PN-G-90105
6 | Underground MV mining outer sheath | Heavy-duty flame-retardant, oil- and tear-resistant polychloroprene (PCP) compound, red | PN-G-90105
| OnGcekgż-G 3.6/6 kV | Medium-voltage screened mining cable for 3.3 kV and 6 kV longwall face machines and mobile transformers.
| OnGcekgż-G 6/10 kV | 10 kV district roadway feeder and mobile substation trailing cable with full radial field control.

## Quality and supply
OnGcekgż-G Screened MV Mining Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekgz-g-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-210. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | MV AC dielectric withstand test — 11 kV rms (3.6/6 kV) or 17 kV rms (6/10 kV) for 5 minutes | Every manufactured drum
Routine test | Partial discharge (PD) measurement — ≤ 20 pC at 1.5 × U0 across full drum length | Every manufactured drum
Sample test | Semi-conductive stress-control resistivity — Inner & outer semicon resistivity verified before/after ageing per PN-G-90105 | Per batch
Type test | Flame propagation & impulse voltage test — Passes PN-EN 60332-1-2 and lightning impulse withstand test | Type approval
Standard / approval | PN-G-90105 / ZN-TF-210
Standard / approval | IEC 60332-1-2
Standard / approval | WUG / CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX OnGcekgż-G 6/10 kV [3×S+1×So+n×s]
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP