## Request a quote
Request a quotation for OnGcekż-G
Specify phase cross-section (10–120 mm²), earth conductor size, number of pilot cores (e.g. 4×2.5 or 7×2.5), and Bretby handler bend radius.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ongcekz-g-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OnGcekż-G Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-g-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90101 / ZN-TF-204. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Power + PE + Control | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| OnGcekż-G 3×10 + 1×10 + 4×1.5 | 3×10 + 1×10 + 4×1.5 | 10 | 29.5 | 442 | 1240 | 177 | Standard OnGcekż-G configurations
| OnGcekż-G 3×16 + 1×16 + 4×2.5 | 3×16 + 1×16 + 4×2.5 | 16 | 33.2 | 710 | 1650 | 199 | Standard OnGcekż-G configurations
| OnGcekż-G 3×25 + 1×16 + 4×2.5 | 3×25 + 1×16 + 4×2.5 | 25 | 36.8 | 970 | 2080 | 221 | Standard OnGcekż-G configurations
| OnGcekż-G 3×35 + 1×16 + 4×2.5 | 3×35 + 1×16 + 4×2.5 | 35 | 39.6 | 1258 | 2510 | 238 | Standard OnGcekż-G configurations
| OnGcekż-G 3×50 + 1×25 + 4×2.5 | 3×50 + 1×25 + 4×2.5 | 50 | 44.2 | 1776 | 3260 | 265 | Standard OnGcekż-G configurations
| OnGcekż-G 3×70 + 1×25 + 4×2.5 | 3×70 + 1×25 + 4×2.5 | 70 | 49 | 2352 | 4120 | 294 | Standard OnGcekż-G configurations
| OnGcekż-G 3×95 + 1×35 + 4×2.5 | 3×95 + 1×35 + 4×2.5 | 95 | 54.5 | 3168 | 5240 | 327 | Standard OnGcekż-G configurations
| OnGcekż-G 3×120 + 1×50 + 4×2.5 | 3×120 + 1×50 + 4×2.5 | 120 | 59.2 | 4032 | 6380 | 355 | Standard OnGcekż-G configurations
| OnGcekż-G 3×50 + 1×25 + 7×2.5 | 3×50 + 1×25 + 7×2.5 | 50 | 45.8 | 1848 | 3440 | 275 | Standard OnGcekż-G configurations
| OnGcekż-G 3×70 + 1×35 + 7×2.5 | 3×70 + 1×35 + 7×2.5 | 70 | 50.6 | 2520 | 4360 | 304 | Standard OnGcekż-G configurations
| OnGcekż-G 3×95 + 1×50 + 7×2.5 | 3×95 + 1×50 + 7×2.5 | 95 | 56 | 3384 | 5520 | 336 | Standard OnGcekż-G configurations
| OnGcekż-G 3×120 + 1×50 + 9×2.5 | 3×120 + 1×50 + 9×2.5 | 120 | 60.8 | 4152 | 6640 | 365 | Standard OnGcekż-G configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90101 / ZN-TF-204.

## Electrical & ampacity data
OnGcekż-G Cable – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-g-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90101 / ZN-TF-204. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
3×10 + 1×10 + 4×1.5 | 1.91 | 70 | 60 | 92 | 3000
3×16 + 1×16 + 4×2.5 | 1.21 | 93 | 79 | 101 | 3000
3×25 + 1×16 + 4×2.5 | 0.78 | 123 | 105 | 114 | 3000
3×35 + 1×16 + 4×2.5 | 0.554 | 152 | 129 | 129 | 3000
3×50 + 1×25 + 4×2.5 | 0.386 | 189 | 161 | 150 | 3000
3×70 + 1×25 + 4×2.5 | 0.272 | 233 | 198 | 180 | 3000
3×95 + 1×35 + 4×2.5 | 0.206 | 282 | 240 | 216 | 3000
3×120 + 1×50 + 4×2.5 | 0.161 | 326 | 277 | 252 | 3000
3×50 + 1×25 + 7×2.5 | 0.386 | 189 | 161 | 150 | 3000
3×70 + 1×35 + 7×2.5 | 0.272 | 233 | 198 | 180 | 3000
3×95 + 1×50 + 7×2.5 | 0.206 | 282 | 240 | 216 | 3000
3×120 + 1×50 + 9×2.5 | 0.161 | 326 | 277 | 252 | 3000
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
OnGcekż-G Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-g-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90101 / ZN-TF-204. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Power cores · 250 V pilot cores)
Key data | Conductor max. | +90 °C (Heat-resistant EPR · +250 °C SC)
Key data | Core screening | Elastomeric 'ek' (Semi-conductive rubber phase screens)
Key data | Min. bend R | 6 × D / 10 × D (Fixed installation / Bretby handler)
Key data | Phase size | 10–120 mm² (Plus PE & 3–9 pilot control cores)
Key data | Flame test | IEC 60332-1-2 (PN-G-90100 underground '-G' sheath)
Electrical | Rated voltage (power cores) | 0.6/1 kV AC (Um 1.2 kV)
Electrical | Rated voltage (pilot cores 'ż') | 250 V AC
Electrical | Routine AC test (power / pilot) | 3.0 kV / 1.5 kV rms for 5 min
Electrical | Semi-conductive screen resistivity | ≤ 500 Ω·m per PN-G-90101
Electrical | Nominal frequency | 50 Hz
Electrical | Earth fault protection | Instantaneous phase-to-screen trip
Thermal | Max. conductor operating temp. | +90 °C continuous ('c' EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range | -25 °C to +60 °C
Thermal | Fixed ambient range | -40 °C to +60 °C
Thermal | Pilot core max. temperature | +90 °C
Thermal | Min. flexing temperature | -25 °C
Mechanical | Min. bend radius (fixed) | 6 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 10 × overall diameter (D)
Mechanical | Bretby handler endurance | Designed for cyclic face travel
Mechanical | Max. dynamic tensile load | 15 N/mm² on power conductors
Mechanical | Crush & rockfall resistance | Heavy-duty '-G' PCP outer jacket
Mechanical | Abrasion resistance | High-tear mining elastomer
Resistance | Flame retardance | IEC 60332-1-2 / PN-G-90100 '-G'
Resistance | Oil & hydraulic emulsion | EN 60811-404 resistant
Resistance | Mine water resistance | Resistant to mineralized mine water
Resistance | Ozone & corona stability | Ozone-free EPR + semi-conductive screen
Resistance | Methane-atmosphere safety | Compatible with IT earth-leakage relays
Resistance | Halogen content | Chloroprene outer sheath
Standards | Primary product standard | PN-G-90101 / ZN-TF-204
Standards | Mining series base standard | PN-G-90100
Standards | Conductor standard | IEC 60228 Class 5
Standards | Flame test standard | PN-EN 60332-1-2
Standards | Mining authority | WUG Poland underground longwall rules
Standards | Quality certificate | EN 10204 3.1 mill certificate
Identification | Phase core identification | Numbered 1, 2, 3 or coloured
Identification | Pilot core identification | Numbered control cores inside screen
Identification | Outer sheath colour | Black or high-visibility yellow
Identification | Sheath marking | Embossed OnGcekż-G 0.6/1 kV PN-G-90101
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Factory lot & year code

## Construction
OnGcekż-G Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-g-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90101 / ZN-TF-204. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase & pilot copper conductors | Class 5 fine-stranded plain or tinned annealed copper (power & control cores) | IEC 60228 Class 5
2 | +90 °C EPR insulation ('c') | Cross-linked heat-resistant ethylene-propylene elastomer on power and control cores | PN-G-90101
3 | Elastomeric core & collective screen | Semi-conductive rubber layer over each power core and over the laid-up control core bundle | PN-G-90101
4 | Auxiliary control unit ('ż') & earth | Screened bundle of 3–9 numbered pilot cores plus uninsulated stranded copper earth | PN-G-90101
5 | Heavy-duty mining outer sheath ('-G') | Flame-retardant, oil- and tear-resistant polychloroprene (PCP) rubber compound, black or | PN-G-90101
| OnGcekż-G 3×S + 1×So + n×s | Three screened phase cores (S), bare earth conductor (So), and screened bundle of 3 to 9 pilot cores (s).
| OnGcekż-G with optical unit | Available with composite fibre-optic control elements for high-speed longwall shearer telemetry.

## Quality and supply
OnGcekż-G Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-g-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90101 / ZN-TF-204. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test on power & pilot cores — 3.0 kV rms (power) and 1.5 kV rms (pilot) for 5 minutes | Every drum
Routine test | Semi-conductive screen resistivity & continuity — Screen contact with earth conductor verified per PN-G-90101 | Every drum
Sample test | Bending & mechanical impact test — No screen cracking or conductor break after cyclic bending | Per batch
Type test | Underground flame & oil resistance — Passes PN-EN 60332-1-2 and EN 60811-404 oil immersion | Type approval
Standard / approval | PN-G-90101 / PN-G-90100
Standard / approval | IEC 60332-1-2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX OnGcekż-G 0.6/1 kV [3×S+1×So+n×s]
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP