## Request a quote
Request a quotation for OnGcekż/w-GW / O2nGcekż/w-GW
Specify OnGcekż/w-GW or O2nGcekż/w-GW, voltage class (1.9/3.3 kV or 3.6/6 kV), phase cross-section (35–95 mm²), and pilot core count (4 or 7 pilots).
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ongcekz-w-gw-o2ngcekz-w-gw-double-screened-mv-mining-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OnGcekż/w-GW / O2nGcekż/w-GW Double-Screened MV Mining Rubber – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-w-gw-o2ngcekz-w-gw-double-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-213. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Type, Voltage & Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| OnGcekż/w-GW 1.9/3.3 kV 3×35+1×16+4×2.5 | 1.9/3.3 kV 3×35+1×16+4×2.5 | 35 | 45.2 | 1340 | 3090 | 271 | OnGcekż/w-GW — Single heavy sheath double-screened water-blocked MV
| OnGcekż/w-GW 1.9/3.3 kV 3×50+1×25+4×2.5 | 1.9/3.3 kV 3×50+1×25+4×2.5 | 50 | 49.8 | 1870 | 3890 | 299 | OnGcekż/w-GW — Single heavy sheath double-screened water-blocked MV
| OnGcekż/w-GW 1.9/3.3 kV 3×70+1×25+4×2.5 | 1.9/3.3 kV 3×70+1×25+4×2.5 | 70 | 54.6 | 2460 | 4820 | 328 | OnGcekż/w-GW — Single heavy sheath double-screened water-blocked MV
| OnGcekż/w-GW 1.9/3.3 kV 3×95+1×35+4×2.5 | 1.9/3.3 kV 3×95+1×35+4×2.5 | 95 | 60.2 | 3290 | 6010 | 361 | OnGcekż/w-GW — Single heavy sheath double-screened water-blocked MV
| OnGcekż/w-GW 3.6/6 kV 3×50+1×25+4×2.5 | 3.6/6 kV 3×50+1×25+4×2.5 | 50 | 53.5 | 1890 | 4280 | 321 | OnGcekż/w-GW — Single heavy sheath double-screened water-blocked MV
| OnGcekż/w-GW 3.6/6 kV 3×70+1×35+4×2.5 | 3.6/6 kV 3×70+1×35+4×2.5 | 70 | 58.4 | 2580 | 5290 | 350 | OnGcekż/w-GW — Single heavy sheath double-screened water-blocked MV
| O2nGcekż/w-GW 1.9/3.3 kV 3×50+1×25+7×2.5 | 1.9/3.3 kV 3×50+1×25+7×2.5 | 50 | 51.6 | 1945 | 4180 | 310 | O2nGcekż/w-GW — Double reinforced sheath double-screened water-blocked MV
| O2nGcekż/w-GW 1.9/3.3 kV 3×70+1×35+7×2.5 | 1.9/3.3 kV 3×70+1×35+7×2.5 | 70 | 56.5 | 2630 | 5160 | 339 | O2nGcekż/w-GW — Double reinforced sheath double-screened water-blocked MV
| O2nGcekż/w-GW 1.9/3.3 kV 3×95+1×50+7×2.5 | 1.9/3.3 kV 3×95+1×50+7×2.5 | 95 | 62 | 3510 | 6420 | 372 | O2nGcekż/w-GW — Double reinforced sheath double-screened water-blocked MV
| O2nGcekż/w-GW 3.6/6 kV 3×50+1×25+7×2.5 | 3.6/6 kV 3×50+1×25+7×2.5 | 50 | 55.2 | 1960 | 4560 | 331 | O2nGcekż/w-GW — Double reinforced sheath double-screened water-blocked MV
| O2nGcekż/w-GW 3.6/6 kV 3×70+1×35+7×2.5 | 3.6/6 kV 3×70+1×35+7×2.5 | 70 | 60.2 | 2650 | 5610 | 361 | O2nGcekż/w-GW — Double reinforced sheath double-screened water-blocked MV
| O2nGcekż/w-GW 3.6/6 kV 3×95+1×50+7×2.5 | 3.6/6 kV 3×95+1×50+7×2.5 | 95 | 65.8 | 3530 | 6920 | 395 | O2nGcekż/w-GW — Double reinforced sheath double-screened water-blocked MV
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90105 / ZN-TF-213.

## Electrical & ampacity data
OnGcekż/w-GW / O2nGcekż/w-GW Double-Screened MV Mining Rubber – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-w-gw-o2ngcekz-w-gw-double-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-213. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
1.9/3.3 kV 3×35+1×16+4×2.5 | 0.554 | 152 | 129 | 129 | 6500
1.9/3.3 kV 3×50+1×25+4×2.5 | 0.386 | 189 | 161 | 150 | 6500
1.9/3.3 kV 3×70+1×25+4×2.5 | 0.272 | 233 | 198 | 180 | 6500
1.9/3.3 kV 3×95+1×35+4×2.5 | 0.206 | 282 | 240 | 216 | 6500
3.6/6 kV 3×50+1×25+4×2.5 | 0.386 | 189 | 161 | 150 | 11000
3.6/6 kV 3×70+1×35+4×2.5 | 0.272 | 233 | 198 | 180 | 11000
1.9/3.3 kV 3×50+1×25+7×2.5 | 0.386 | 189 | 161 | 150 | 6500
1.9/3.3 kV 3×70+1×35+7×2.5 | 0.272 | 233 | 198 | 180 | 6500
1.9/3.3 kV 3×95+1×50+7×2.5 | 0.206 | 282 | 240 | 216 | 6500
3.6/6 kV 3×50+1×25+7×2.5 | 0.386 | 189 | 161 | 150 | 11000
3.6/6 kV 3×70+1×35+7×2.5 | 0.272 | 233 | 198 | 180 | 11000
3.6/6 kV 3×95+1×50+7×2.5 | 0.206 | 282 | 240 | 216 | 11000
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
OnGcekż/w-GW / O2nGcekż/w-GW Double-Screened MV Mining Rubber – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-w-gw-o2ngcekz-w-gw-double-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-213. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.9/3.3 & 3.6/6 (High-power longwall shearer MV)
Key data | Double screen | Phase + overall (Individual 'ek' + collective screen)
Key data | Water blocking | Sealed '-GW' (Longitudinal hydro-swelling barriers)
Key data | Conductor max. | +90 °C (MV EPR dielectric · +250 °C SC)
Key data | Min. bend R | 6 × D / 10 × D (Fixed installation / Bretby handler)
Key data | Sheath options | On / O2n '-GW' (Single or double reinforced PCP)
Electrical | Rated voltage U0/U | 1.9/3.3 kV or 3.6/6 kV AC
Electrical | Maximum system voltage Um | 3.6 kV or 7.2 kV AC
Electrical | Routine AC test voltage | 6.5 kV (3.3 kV) / 11 kV (6 kV)
Electrical | Double screening architecture | Per-core 'ek' + overall '/w' screen
Electrical | Pilot core rated voltage | 250 V AC
Electrical | Partial discharge level | ≤ 20 pC at 1.5 × U0
Thermal | Max. conductor operating temp. | +90 °C continuous ('c' MV EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range | -25 °C to +60 °C
Thermal | Fixed ambient range | -40 °C to +60 °C
Thermal | Max. water immersion temp. | +40 °C continuous
Thermal | Min. laying temperature | -15 °C
Mechanical | Min. bend radius (fixed) | 6 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 10 × overall diameter (D)
Mechanical | Max. tensile pull (On / O2n) | 15 N/mm² (On) / 25 N/mm² (O2n)
Mechanical | Penetration & crush safety | Dual concentric earth screens
Mechanical | Longitudinal water tightness | Sealed '-GW' swelling barriers
Mechanical | Tear resistance | ≥ 20 N/mm on O2n sheath
Resistance | Water & moisture ingress | Sealed '-GW' water-blocked
Resistance | Flame retardance | IEC 60332-1-2 / PN-G-90100
Resistance | Mineral oil & hydraulic fluid | EN 60811-404 resistant PCP
Resistance | Ozone & corona stability | PD-free MV EPR dielectric
Resistance | Methane-atmosphere protection | Redundant '/w' earth-leakage screen
Resistance | Halogen status | Polychloroprene elastomer
Standards | Primary product standard | PN-G-90105 / ZN-TF-213
Standards | Mining series base standard | PN-G-90100
Standards | Conductor standard | IEC 60228 Class 5
Standards | Flame propagation test | PN-EN 60332-1-2
Standards | Mining authority compliance | WUG Poland 3.3/6 kV wet-face rules
Standards | Quality certification | EN 10204 3.1 + PD routine test
Identification | Phase core identification | Numbered 1, 2, 3
Identification | Pilot core identification | Numbered control cores in screened unit
Identification | Outer sheath colour | Red, yellow, or black
Identification | Sheath marking | O2nGcekż/w-GW [U0/U] PN-G-90105
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Drum serial & HV test report

## Construction
OnGcekż/w-GW / O2nGcekż/w-GW Double-Screened MV Mining Rubber – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-w-gw-o2ngcekz-w-gw-double-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-213. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper phase & pilot conductors | Class 5 fine-stranded plain or tinned copper with water-blocking yarns | IEC 60228 Class 5
2 | +90 °C MV EPR dielectric ('c') | Triple-extruded medium-voltage ethylene-propylene elastomer with inner semicon | PN-G-90105
3 | Individual core elastomeric/Cu screens | Semi-conductive elastomer and copper screen over each phase core and over the pilot | PN-G-90105
4 | Hydro-swelling water barrier ('W') | Longitudinal water-swellable tapes over the laid-up core assembly | ZN-TF-213
5 | Collective overall second screen ('/w') | Overall semi-conductive elastomeric/copper braid penetration barrier enclosing the | ZN-TF-213
6 | Single ('On') or double ('O2n') '-GW' | Heavy-duty flame-retardant, water-sealed polychloroprene outer sheath (reinforced double | PN-G-90105
| OnGcekż/w-GW (1.9/3.3 & 3.6/6 kV) | Double-screened water-blocked MV trailing cable with single heavy-duty '-GW' polychloroprene outer sheath.
| O2nGcekż/w-GW (1.9/3.3 & 3.6/6 kV) | Double-screened water-blocked MV trailing cable with double-layer reinforced ('O2n') polychloroprene outer

## Quality and supply
OnGcekż/w-GW / O2nGcekż/w-GW Double-Screened MV Mining Rubber – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcekz-w-gw-o2ngcekz-w-gw-double-screened-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-213. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | MV AC voltage withstand test — 6.5 kV rms (1.9/3.3 kV) or 11 kV rms (3.6/6 kV) for 5 minutes | Every drum
Routine test | Inner & outer ('/w') screen continuity — Both per-core and collective screens verified for earth continuity | Every drum
Sample test | Hydrostatic longitudinal water-blocking test — Zero water propagation along core interstices per '-GW' spec | Per batch
Type test | Nail/wedge penetration & flame test — Outer '/w' screen trips earth relay before phase contact; passes IEC 60332-1-2 | Type approval
Standard / approval | PN-G-90105 / ZN-TF-213
Standard / approval | IEC 60332-1-2
Standard / approval | WUG / CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX O2nGcekż/w-GW 1.9/3.3 kV
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP