## Request a quote
Request a quotation for OnGcrekgż-G(S) / OnGcrekgż-G(Z)
Specify series — (S) for roadway gallery installation or (Z) for reinforced mobile trailing/reeling — voltage (3.6/6 or 6/10 kV), and phase cross-section.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ongcrekgz-g-s-ongcrekgz-g-z-s-z-series-mv-mining-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
OnGcrekgż-G(S) / OnGcrekgż-G(Z) S/Z-Series MV Mining Rubber Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcrekgz-g-s-ongcrekgz-g-z-s-z-series-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-212. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Series, Voltage & Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| OnGcrekgż-G(S) 3.6/6 kV 3×25+1×16+1×6 | 3.6/6 kV 3×25+1×16+1×6 | 25 | 44 | 1020 | 2680 | 264 | OnGcrekgż-G(S) — Roadway & semi-fixed MV mining feeder series
| OnGcrekgż-G(S) 3.6/6 kV 3×35+1×16+1×6 | 3.6/6 kV 3×35+1×16+1×6 | 35 | 46.8 | 1315 | 3150 | 281 | OnGcrekgż-G(S) — Roadway & semi-fixed MV mining feeder series
| OnGcrekgż-G(S) 3.6/6 kV 3×50+1×25+1×6 | 3.6/6 kV 3×50+1×25+1×6 | 50 | 51.6 | 1845 | 3980 | 310 | OnGcrekgż-G(S) — Roadway & semi-fixed MV mining feeder series
| OnGcrekgż-G(S) 6/10 kV 3×50+1×25+1×6 | 6/10 kV 3×50+1×25+1×6 | 50 | 56 | 1860 | 4460 | 336 | OnGcrekgż-G(S) — Roadway & semi-fixed MV mining feeder series
| OnGcrekgż-G(S) 6/10 kV 3×70+1×35+1×6 | 6/10 kV 3×70+1×35+1×6 | 70 | 60.8 | 2540 | 5490 | 365 | OnGcrekgż-G(S) — Roadway & semi-fixed MV mining feeder series
| OnGcrekgż-G(S) 6/10 kV 3×95+1×50+1×6 | 6/10 kV 3×95+1×50+1×6 | 95 | 66.5 | 3420 | 6810 | 399 | OnGcrekgż-G(S) — Roadway & semi-fixed MV mining feeder series
| OnGcrekgż-G(Z) 3.6/6 kV 3×25+1×16+1×6 | 3.6/6 kV 3×25+1×16+1×6 | 25 | 45.6 | 1020 | 2860 | 274 | OnGcrekgż-G(Z) — Reinforced trailing & dynamic MV mining series
| OnGcrekgż-G(Z) 3.6/6 kV 3×35+1×16+1×6 | 3.6/6 kV 3×35+1×16+1×6 | 35 | 48.5 | 1315 | 3360 | 291 | OnGcrekgż-G(Z) — Reinforced trailing & dynamic MV mining series
| OnGcrekgż-G(Z) 3.6/6 kV 3×50+1×25+1×6 | 3.6/6 kV 3×50+1×25+1×6 | 50 | 53.4 | 1845 | 4220 | 320 | OnGcrekgż-G(Z) — Reinforced trailing & dynamic MV mining series
| OnGcrekgż-G(Z) 3.6/6 kV 3×70+1×35+1×6 | 3.6/6 kV 3×70+1×35+1×6 | 70 | 58.2 | 2540 | 5210 | 349 | OnGcrekgż-G(Z) — Reinforced trailing & dynamic MV mining series
| OnGcrekgż-G(Z) 6/10 kV 3×50+1×25+1×6 | 6/10 kV 3×50+1×25+1×6 | 50 | 57.8 | 1860 | 4720 | 347 | OnGcrekgż-G(Z) — Reinforced trailing & dynamic MV mining series
| OnGcrekgż-G(Z) 6/10 kV 3×70+1×35+1×6 | 6/10 kV 3×70+1×35+1×6 | 70 | 62.6 | 2540 | 5780 | 376 | OnGcrekgż-G(Z) — Reinforced trailing & dynamic MV mining series
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90105 / ZN-TF-212.

## Electrical & ampacity data
OnGcrekgż-G(S) / OnGcrekgż-G(Z) S/Z-Series MV Mining Rubber Cable – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcrekgz-g-s-ongcrekgz-g-z-s-z-series-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-212. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
3.6/6 kV 3×25+1×16+1×6 | 0.78 | 123 | 105 | 114 | 11000
3.6/6 kV 3×35+1×16+1×6 | 0.554 | 152 | 129 | 129 | 11000
3.6/6 kV 3×50+1×25+1×6 | 0.386 | 189 | 161 | 150 | 11000
6/10 kV 3×50+1×25+1×6 | 0.386 | 189 | 161 | 150 | 17000
6/10 kV 3×70+1×35+1×6 | 0.272 | 233 | 198 | 180 | 17000
6/10 kV 3×95+1×50+1×6 | 0.206 | 282 | 240 | 216 | 17000
3.6/6 kV 3×25+1×16+1×6 | 0.78 | 123 | 105 | 114 | 11000
3.6/6 kV 3×35+1×16+1×6 | 0.554 | 152 | 129 | 129 | 11000
3.6/6 kV 3×50+1×25+1×6 | 0.386 | 189 | 161 | 150 | 11000
3.6/6 kV 3×70+1×35+1×6 | 0.272 | 233 | 198 | 180 | 11000
6/10 kV 3×50+1×25+1×6 | 0.386 | 189 | 161 | 150 | 17000
6/10 kV 3×70+1×35+1×6 | 0.272 | 233 | 198 | 180 | 17000
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
OnGcrekgż-G(S) / OnGcrekgż-G(Z) S/Z-Series MV Mining Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcrekgz-g-s-ongcrekgz-g-z-s-z-series-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-212. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 & 6/10 kV (Um 7.2 kV / 12 kV MV mining)
Key data | Radial screen | Cu + semicon 'r' (High earth-fault current capacity)
Key data | Series options | (S) & (Z) types ((S) roadway / (Z) reinforced trailing)
Key data | Conductor max. | +90 °C (MV EPR dielectric · +250 °C SC)
Key data | Min. bend R | 6 × D / 10 × D (Fixed (S) / mobile trailing (Z))
Key data | Flame test | IEC 60332-1-2 (Underground '-G' PCP compound)
Electrical | Rated voltage U0/U | 3.6/6 kV or 6/10 kV AC
Electrical | Maximum system voltage Um | 7.2 kV or 12.0 kV AC
Electrical | Routine AC test voltage | 11 kV (3.6/6 kV) / 17 kV (6/10 kV)
Electrical | Partial discharge level | ≤ 20 pC at 1.5 × U0
Electrical | Metallic radial screen ('r') | Low-impedance copper wire/braid screen
Electrical | Pilot core voltage rating | 250 V AC
Thermal | Max. conductor operating temp. | +90 °C continuous ('c' MV EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range | -25 °C to +60 °C
Thermal | Fixed ambient range | -40 °C to +60 °C
Thermal | Min. laying temperature | -15 °C
Thermal | Metallic screen SC rating | +200 °C earth-fault thermal limit
Mechanical | Min. bend radius (S-series) | 6 × overall diameter (D)
Mechanical | Min. bend radius (Z-series) | 10 × overall diameter (D)
Mechanical | Max. tensile pull (S / Z) | 15 N/mm² (S) / 25 N/mm² (Z)
Mechanical | Torsional stability (Z-series) | ±50 °/m anti-twist braid
Mechanical | Crush & impact resistance | Heavy underground '-G' PCP sheath
Mechanical | Tear resistance | ≥ 18 N/mm (Z-series)
Resistance | Flame retardance | IEC 60332-1-2 / PN-G-90100 '-G'
Resistance | Mineral oil & hydraulic emulsion | EN 60811-404 resistant PCP
Resistance | Ozone & partial discharge | Triple-extruded MV EPR + 'rekg'
Resistance | Mine water & humidity | Acidic/alkaline mine water resistant
Resistance | EMC & radial field containment | 100 % radial electric field control
Resistance | Halogen status | Polychloroprene elastomer
Standards | Primary product standard | PN-G-90105 / ZN-TF-212
Standards | Mining series base standard | PN-G-90100
Standards | Conductor standard | IEC 60228 Class 5
Standards | Flame propagation test | PN-EN 60332-1-2
Standards | Mining authority compliance | WUG Poland MV underground rules
Standards | Quality certification | EN 10204 3.1 + PD routine test
Identification | Phase core identification | Numbered 1, 2, 3
Identification | Pilot core identification | Screened auxiliary control core
Identification | Outer sheath colour | Red or black
Identification | Sheath marking | OnGcrekgż-G(S) or (Z) [U0/U] PN-G-90105
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Drum serial & HV test certificate

## Construction
OnGcrekgż-G(S) / OnGcrekgż-G(Z) S/Z-Series MV Mining Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcrekgz-g-s-ongcrekgz-g-z-s-z-series-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-212. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper phase conductor | Class 5 fine-stranded plain or tinned annealed copper wire | IEC 60228 Class 5
2 | Inner conductor stress-control layer | Extruded semi-conductive rubber layer bonded to insulation | PN-G-90105
3 | +90 °C MV EPR dielectric ('c') | Ozone- and PD-resistant medium-voltage ethylene-propylene elastomer | PN-G-90105
4 | Outer semicon + radial copper screen | Semi-conductive rubber layer plus helically lapped/braided annealed copper wire radial | PN-G-90105 / ZN-TF-212
5 | Pilot core ('ż') & earth conductor | Screened auxiliary control core and bare flexible copper earth conductor | PN-G-90105
6 | Anti-torsion reinforcement braid | High-tenacity synthetic reinforcement braid vulcanised between inner and outer sheaths | ZN-TF-212
7 | Underground MV mining PCP sheath ('-G') | Heavy-duty flame-retardant, oil-resistant polychloroprene outer jacket, red or black | PN-G-90105
| OnGcrekgż-G(S) | S-Series for roadway gallery hangers and semi-stationary connections between underground MV switchgear and
| OnGcrekgż-G(Z) | Z-Series with embedded anti-torsion/anti-crush reinforcement braid for mobile trailing and drum-reeled MV

## Quality and supply
OnGcrekgż-G(S) / OnGcrekgż-G(Z) S/Z-Series MV Mining Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ongcrekgz-g-s-ongcrekgz-g-z-s-z-series-mv-mining-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90105 / ZN-TF-212. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | MV AC voltage withstand test — 11 kV rms (3.6/6 kV) or 17 kV rms (6/10 kV) for 5 minutes | Every drum
Routine test | Partial discharge & radial screen resistance — PD ≤ 20 pC at 1.5 × U0; copper radial screen DC resistance verified | Every drum
Sample test | Tensile & torsional flex test (Z-series) — No copper screen strand breakage after cyclic bending under tension | Per batch
Type test | Flame propagation & earth-fault current test — Passes PN-EN 60332-1-2 and radial screen short-circuit rating | Type approval
Standard / approval | PN-G-90105 / ZN-TF-212
Standard / approval | IEC 60332-1-2
Standard / approval | WUG / CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX OnGcrekgż-G(Z) 6/10 kV
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP