## Request a quote
Request a quotation for PROFIBUS DP
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for PROFIBUS DP.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/profibus-dp-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
PROFIBUS DP Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-dp-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 / EN 50170 (PROFIBUS DP Type A). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| PROFIBUS DP FC Standard PVC 1×2×0.64 | 1×2×0.64 mm (Fixed PVC Violet) | 0.64 mm (AWG 22/1) | 8 | 26 | 66 | 64 | Standard PROFIBUS DP configurations
| PROFIBUS DP FC FRNC/LSZH 1×2×0.64 | 1×2×0.64 mm (Fixed LSZH Violet) | 0.64 mm (AWG 22/1) | 8 | 26 | 68 | 64 | Standard PROFIBUS DP configurations
| PROFIBUS DP FC Ex-i Blue 1×2×0.64 | 1×2×0.64 mm (Ex-i Blue PVC) | 0.64 mm (AWG 22/1) | 8 | 26 | 66 | 64 | Standard PROFIBUS DP configurations
| PROFIBUS DP Underground PE 2Y2Y 1×2×0.64 | 1×2×0.64 mm (Burial Black PE) | 0.64 mm (AWG 22/1) | 8 | 26 | 58 | 64 | Standard PROFIBUS DP configurations
| PROFIBUS DP FC Flex 1×2×0.78 (7-wire) | 1×2×0.78 mm (7-wire Flex PUR) | 0.34 mm² (AWG 22/7) | 8 | 28 | 64 | 64 | Standard PROFIBUS DP configurations
| PROFIBUS DP Drag-Chain Trailing PUR 1×2×0.78 (19-wire) | 1×2×0.78 mm (19-wire Chain PUR) | 0.36 mm² (AWG 22/19) | 8 | 28 | 63 | 64 | Standard PROFIBUS DP configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per IEC 61158-2 / EN 50170 (PROFIBUS DP Type A).

## Impedance, capacitance & attenu
PROFIBUS DP Cable – Impedance, capacitance & attenuation (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-dp-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 / EN 50170 (PROFIBUS DP Type A). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
1×2×0.64 mm (Fixed PVC Violet) | 150 Ω | 110 | 28.5 | 79 | 0.25 @ 0.2 · 2.2 @ 4 · 4.2 @ 16 MHz | 1500
1×2×0.64 mm (Fixed LSZH Violet) | 150 Ω | 110 | 28.5 | 79 | 0.25 @ 0.2 · 2.2 @ 4 · 4.2 @ 16 MHz | 1500
1×2×0.64 mm (Ex-i Blue PVC) | 150 Ω | 110 | 28.5 | 79 | 0.25 @ 0.2 · 2.2 @ 4 · 4.2 @ 16 MHz | 1500
1×2×0.64 mm (Burial Black PE) | 150 Ω | 110 | 28.5 | 79 | 0.25 @ 0.2 · 2.2 @ 4 · 4.2 @ 16 MHz | 1500
1×2×0.78 mm (7-wire Flex PUR) | 150 Ω | 133 | 28.5 | 78 | 0.30 @ 0.2 · 2.5 @ 4 · 4.9 @ 16 MHz | 1500
1×2×0.78 mm (19-wire Chain PUR) | 150 Ω | 133 | 28.5 | 78 | 0.30 @ 0.2 · 2.5 @ 4 · 4.9 @ 16 MHz | 1500
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per IEC 61158-2 / EN 50170 (PROFIBUS DP Type A).

## Technical data
PROFIBUS DP Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-dp-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 / EN 50170 (PROFIBUS DP Type A). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance Z0 | 150 Ω ± 15 Ω (Measured at 3 to 20 MHz)
Key data | Capacitance | < 30 pF / m (≈ 28.5 pF/m foamed PE O2YS)
Key data | Data rate | Up to 12 Mbps (100 m @ 12 Mbps · 1200 m @ 93.75 kbps)
Key data | Loop resistance | ≤ 110 Ω / km (Line A (Green) + Line B (Red))
Key data | FastConnect OD | 8.0 mm ± 0.4 (Fits 9-pin D-Sub & M12 B-coded FC)
Key data | Sheath options | PVC / PUR / PE (RAL 4001 Violet · Black PE · Blue Ex-i)
Electrical | Characteristic impedance Z0 | 150 Ω ± 15 Ω (3 to 20 MHz)
Electrical | Low-frequency impedance (31.25–39 | 185 Ω ± 18.5 Ω
Electrical | Max. DC loop resistance @ 20 °C | ≤ 110 Ω/km (solid 0.64 mm) · ≤ 133 Ω/km
Electrical | Mutual capacitance @ 1 kHz | ≈ 28.5 pF/m (standard limit < 30 pF/m)
Electrical | Velocity of propagation (VoP) | 78–80 % (0.78–0.80 c)
Electrical | Attenuation (0.2 / 4 / 16 MHz) | 0.25 / 2.2 / 4.2 dB/100m (solid Type A)
Thermal | Operating temp. (fixed / flex) | -40 °C to +80 °C fixed · -30 °C to +70 °C
Thermal | Operating / test voltage | 250 V (300 V UL CMG) · 1.5 kV AC / 3.6 kV
Mechanical | Outer diameter (FastConnect) | 8.0 mm ± 0.4 mm
Mechanical | Min. bending radius (fixed / chain) | 7.5 × D (60 mm) fixed · 10 × D (80 mm)
Resistance | Oil & chemical resistance | EN 60811-404 · UL Oil Res I/II (PUR &
Resistance | Flame & halogen-free | IEC 60332-1-2 · UL CMG/PLTC · FRNC IEC 60754
Standards | Primary specification | IEC 61158-2 / EN 50170-2-2 PROFIBUS Type A
Standards | Hazardous area option | EN 60079-14 Intrinsic Safety Ex-i (RAL 5015
Identification | Core colours | Green (Data Line A) · Red (Data Line B)
Identification | Outer sheath colour | RAL 4001 Red-Lilac (Violet) · Black (PE) ·

## Construction
PROFIBUS DP Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-dp-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 / EN 50170 (PROFIBUS DP Type A). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Copper conductor pair | Ø 0.64 mm solid bare Cu (fixed) or Ø 0.78 mm 7-wire / 19-wire stranded Cu (flex | IEC 61158-2 / EN 50170
2 | Foamed-skin PE (O2YS) dielectric | Cellular polyethylene insulation (Ø 2.55 mm) yielding < 30 pF/m and Z0 = 150 Ω | EN 50170 Type A
3 | FastConnect inner bedding | Extruded thermoplastic filler jacket holding Green/Red cores at exact IDC pitch
4 | Static screen (Al/PET) | Aluminium-laminated polyester tape (100 % coverage, metal side outward) | IEC 61158-2
5 | EMC tinned copper braid | Tinned copper wire braid over Al/PET foil | IEC 61158-2
6 | Outer sheath (8.0 mm OD) | RAL 4001 Violet PVC, PUR, or LSZH; RAL 9005 Black PE (burial); RAL 5015 Blue (Ex-i)
| PROFIBUS DP FC Standard (PVC / PUR / FRNC) | 1×2×0.64 mm solid FastConnect cable in RAL 4001 violet (or Blue Ex-i / Black PE underground).
| PROFIBUS DP Flex & Drag-Chain (7-wire / 19-wire PUR) | 1×2×0.78 mm stranded FastConnect cable for vibrating machinery and ≥ 5M-cycle drag chains.

## Quality and supply
PROFIBUS DP Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-dp-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 / EN 50170 (PROFIBUS DP Type A). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3–20 MHz characteristic impedance & attenuation sweep — Z0 = 150 ± 15 Ω; ≤ 4.2 dB/100m at 16 MHz | 100 % of reels
Routine test | Mutual capacitance & DC loop resistance — < 30 pF/m at 1 kHz; ≤ 110 Ω/km (solid) | 100 % of reels
Sample test | FastConnect stripping & Sub-D IDC contact test — Zero shield strand bridging & stable IDC contact | Per production batch
Type test | Drag-chain endurance (Trailing PUR variant) — ≥ 5,000,000 bending cycles at 10 × D | Type approval
Standard / approval | IEC 61158-2 / EN 50170
Standard / approval | PNO FastConnect Spec
Standard / approval | UL CMG / PLTC / AWM
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX PROFIBUS DP FASTCONNECT
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP